## index
Normal Time | % | Completed
Pressure
Flow
Temperature
Level
Calibrated Total
Waiting Total
Total Tx
KIPP00*
KIPP10*
KIPP11*
KIPP12*

## Tx Detail List
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
No | Group | Functional Location | Description | Calibration Date | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No. | Tx Status | SAP Ekipman Kodu | Order Type | SAP Status | Full Model Number | Panel KKS | Comments
1 | KIPP00 | 00GHC01CP101 | DEMIN WATER PUMP-A SUCTION PRESS. | 2026-04-13 | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313262 |  |  | ZM06
2 | KIPP00 | 00GHC01CP102 | DEMIN WATER PUMP-A SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313090 |  |  | ZM06
3 | KIPP00 | 00GHC02CP101 | DEMIN WATER PUMP-B SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313263 |  |  | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
4 | KIPP00 | 00GHC02CP102 | DEMIN WATER PUMP-B SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313091 |  |  | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
5 | KIPP00 | 00GHC03CP101 | DEMIN WATER PUMP-C SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313264 |  |  | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
6 | KIPP00 | 00GHC03CP102 | DEMIN WATER PUMP-C SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313092 |  |  | ZM06 |  |  | 10LAB01GH101
7 | KIPP00 | 00GHC04CP101 | EMERGENCY M/U PUMP-A SUCTION PT |  | -1 | 100 | -1 | 5 | Bar | YOKOGAWA | EJA530E | 91S313216 |  |  | ZM06 |  |  | 10LAB02GH101
8 | KIPP00 | 00GHC04CP102 | EMERGENCY M/U PUMP-A SUCTION STRAINER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313106 |  |  | ZM06 |  |  | 10LAB02GH101
9 | KIPP00 | 00GHC05CP101 | EMERGENCY M/U PUMP-B SUCTION PT |  | -1 | 100 | -1 | 5 | Bar | YOKOGAWA | EJA530E | 91S313214 |  |  | ZM06 |  |  | 10LAB06GH101
10 | KIPP00 | 00GHC05CP102 | EMERGENCY M/U PUMP-B SUCTION STRAINER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313105 |  |  | ZM06 |  |  | 10LAB06GH101
11 | KIPP00 | 00GHC10CP101 | DEMIN. WATER SUPPLY PUMP DISC. PRESS. A | 2026-01-29 | -1 | 20 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313246 |  |  | ZM06 |  |  | 10LAB06GH101
12 | KIPP00 | 00GHC10CP102 | DEMIN. WATER SUPPLY PUMP DISC. PRESS. B | 2026-01-29 | -1 | 20 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313247 |  |  | ZM06 |  |  | 10LAB10GH101
13 | KIPP00 | 00GHC16CP101 | EMERGENCY M/U DISCAHARGE PT - A |  | -1 | 100 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313302 |  |  | ZM06 |  |  | 10LAB10GH101
14 | KIPP00 | 00GHC16CP102 | EMERGENCY M/U DISCAHARGE PT - B |  | -1 | 100 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313303 |  |  | ZM06 |  |  | 10LAB01GH101
15 | KIPP00 | 00GHC24CF101 | CONDENSER MAKE UP WATER FIT |  | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313065 |  |  | ZM06 |  |  | 10LAB02GH101
16 | KIPP00 | 00GKB21CP101 | POTABLE WATER SUPPLY PUMP-A SUCTION PT |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313267 |  |  | ZM06 |  |  | 00GKB21GH01
17 | KIPP00 | 00GKB22CP101 | POTABLE WATER SUPPLY PUMP-B SUCTION PT |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313268 |  |  | ZM06 |  |  | 00GKB21GH01
18 | KIPP00 | 00GKB30CP101 | POTABLE WATER SUPPLY PUMP DISCHARGE PT - A |  | -1 | 20 | 0 | 9 | Bar | YOKOGAWA | EJA530E | 91S313244 |  |  | ZM06 |  |  | 00GKB21GH01
19 | KIPP00 | 00GKB30CP102 | POTABLE WATER SUPPLY PUMP DISCHARGE PT - B |  | -1 | 20 | 0 | 9 | Bar | YOKOGAWA | EJA530E | 91S313245 |  |  | ZM06 |  |  | 00GKB21GH01
20 | KIPP10 | 10LAA00CL101 | DEAERATOR & FW STORAGE TANK LEVEL A |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313099 |  |  | ZM06 |  |  | 10LAB15GH101
21 | KIPP10 | 10LAA00CL102 | DEAERATOR & FW STORAGE TANK LEVEL B |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313098 |  |  | ZM06 |  |  | 10LAB15GH101
22 | KIPP10 | 10LAA00CL103 | DEAERATOR & FW STORAGE TANK LEVEL C |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313095 |  |  | ZM06 |  |  | 10LAB10GH101
23 | KIPP10 | 10LAA00CL104 | DEAERATOR & FW STORAGE TANK LEVEL D |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313094 |  |  | ZM06 |  |  | 10LAB10GH101
24 | KIPP10 | 10LAA00CL105 | DEAERATOR & FW STORAGE TANK LEVEL E |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313093 |  |  | ZM06 |  |  | 10LAB01GH101
25 | KIPP10 | 10LAA00CP101 | DEAERATOR & FW STORAGE TANK PRESSURE A |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313278 |  |  | ZM06 |  |  | 10LAB02GH101
26 | KIPP10 | 10LAA00CP102 | DEAERATOR & FW STORAGE TANK PRESSURE B |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313279 |  |  | ZM06 |  |  | 10LAB02GH101
27 | KIPP10 | 10LAA00CP103 | DEAERATOR & FW STORAGE TANK PRESSURE C |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313280 |  |  | ZM06 |  |  | 10LAB02GH101
28 | KIPP10 | 10LAB01CP102 | STG 10 BOILER FWP C SUCTION PRESSURE |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213232 |  |  | ZM06
29 | KIPP10 | 10LAB02CP102 | BOILER FEED WATER PUMP B SUCTION PT |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213233 |  |  | ZM06
30 | KIPP10 | 10LAB03CP102 | STG 10 BOILER FWP C SUCTION PRESSURE |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213234 |  |  | ZM06
31 | KIPP10 | 10LAB06CP102 | CPH PUMP-A SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313235 |  |  | ZM06
32 | KIPP10 | 10LAB07CP102 | CPH PUMP-B SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313236 |  |  | ZM06
33 | KIPP10 | 10LAB08CP102 | CPH PUMP-C SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313237 |  |  | ZM06
34 | KIPP10 | 10LAB10CP101 | BOILER FEED WATER PUMP-A HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S313320 |  |  | ZM06 |  |  | 10LAB10GH101
35 | KIPP10 | 10LAB10CP102 | BOILER FEED WATER PUMP-B HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S313321 |  |  | ZM06 |  |  | 10LAB10GH101
36 | KIPP10 | 10LAB11CF101 | BOILER FEED WATER PUMP A HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313539 |  |  | ZM06
37 | KIPP10 | 10LAB11CF102 | BOILER FEED WATER PUMP A HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313542 |  |  | ZM06
38 | KIPP10 | 10LAB11CP101 | BOILER FEED WATER PUMP-A HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213317 |  |  | ZM06
39 | KIPP10 | 10LAB12CF101 | BOILER FEED WATER PUMP B HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313540 |  |  | ZM06
40 | KIPP10 | 10LAB12CF102 | BOILER FEED WATER PUMP B HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313543 |  |  | ZM06
41 | KIPP10 | 10LAB12CP101 | BOILER FEED WATER PUMP-B HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213318 |  |  | ZM06
42 | KIPP10 | 10LAB13CF101 | BOILER FEED WATER PUMP C HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313541 |  |  | ZM06
43 | KIPP10 | 10LAB13CF102 | BOILER FEED WATER PUMP C HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313544 |  |  | ZM06
44 | KIPP10 | 10LAB13CP101 | BOILER FEED WATER PUMP-C HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213319 |  |  | ZM06
45 | KIPP10 | 10LAB15CP101 | CPH PUMP DISCHARGE LINE PT A |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313311 |  |  | ZM06
46 | KIPP10 | 10LAB15CP102 | CPH PUMP DISCHARGE LINE PT B |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313312 |  |  | ZM06
47 | KIPP10 | 10LAB16CP101 | CPH PUMP-A DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S213304 |  |  | ZM06
48 | KIPP10 | 10LAB17CP101 | CPH PUMP-B DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313305 |  |  | ZM06
49 | KIPP10 | 10LAB18CP101 | CPH PUMP-C DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313306 |  |  | ZM06
50 | KIPP10 | 10LAB24CF101 | CRH STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 2500 | mmH2O | YOKOGAWA | EJA110E | 91S313064 |  |  | ZM06
51 | KIPP10 | 10LAB30CP101 | BOILER FEED WATER PUMP IP DISCHARGE PT-A |  | -1 | 500 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313218 |  |  | ZM06 |  |  | 10LAB10GH101
52 | KIPP10 | 10LAB30CP102 | BOILER FEED WATER PUMP IP DISCHARGE PT-B |  | -1 | 500 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313220 |  |  | ZM06 |  |  | 10LAB10GH101
53 | KIPP10 | 10LAB31CP101 | BFWP A IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313299 |  |  | ZM06
54 | KIPP10 | 10LAB32CP101 | BFWP B IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313300 |  |  | ZM06
55 | KIPP10 | 10LAB33CP101 | BFWP C IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313301 |  |  | ZM06
56 | KIPP10 | 10LBA10CP001 | P LP STEAM BFR ST | 2026-03-23 | -1 | 20 | -1 | 10 | Bar | YOKOGAWA | EJA530E | 91S313251 |  |  | ZM06
57 | KIPP10 | 10LBA10CP002 | P LP STEAM BFR ST | 2026-03-23 | -1 | 20 | -1 | 10 | Bar | YOKOGAWA | EJA530E | 91S313252 |  |  | ZM06
58 | KIPP10 | 10LBA50CP001 | P HP STEAM BFR ST | 2026-03-18 | -1 | 500 | -1 | 150 | Bar | YOKOGAWA | EJA530E | 91S313322 |  |  | ZM06 |  |  | STG BINASI ZEMIN
59 | KIPP10 | 10LBA50CP002 | P HP STEAM BFR ST | 2026-03-18 | -1 | 500 | -1 | 150 | Bar | YOKOGAWA | EJA530E | 91S313323 |  |  | ZM06 |  |  | STG BINASI ZEMIN
60 | KIPP10 | 10LBB41CP001 | P IP STEAM BFR ST | 2026-03-18 | -1 | 100 | -1 | 40 | Bar | YOKOGAWA | EJA530E | 91S313307 |  |  | ZM06
61 | KIPP10 | 10LBB42CP001 | P IP STEAM BFR ST | 2026-03-18 | -1 | 100 | -1 | 40 | Bar | YOKOGAWA | EJA530E | 91S313308 |  |  | ZM06
62 | KIPP10 | 10LBC10CP001 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313289 |  |  | ZM06
63 | KIPP10 | 10LBC10CP002 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313290 |  |  | ZM06
64 | KIPP10 | 10LBC10CP003 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313291 |  |  | ZM06
65 | KIPP10 | 10LBC10CP101 | STG 10 COLD REHEAT STEAM PRESS. | 2026-03-18 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313286 |  |  | ZM06
66 | KIPP10 | 10LBG00CP101 | AUXILIARY STEAM LINE PRESS. | 2026-03-23 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313292 |  |  | ZM06
67 | KIPP10 | 10LBG00CP102 | AUXILIARY STEAM LINE PRESS. | 2026-03-23 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313293 |  |  | ZM06
68 | KIPP10 | 10LCA01CP102 | CONDENSATE EXTRACTION PUMP-A SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313253 |  |  | ZM06
69 | KIPP10 | 10LCA02CP102 | CONDENSATE EXTRACTION PUMP-B SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313254 |  |  | ZM06
70 | KIPP10 | 10LCA03CP102 | CONDENSATE EXTRACTION PUMP-C SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313255 |  |  | ZM06
71 | KIPP10 | 10LCA10CF101 | CONDENSATE EXTRACTION PUMP DISCHARGE FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313066 |  |  | ZM06
72 | KIPP10 | 10LCA10CF102 | CONDENSATE EXTRACTION PUMP DISCHARGE FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313101 |  |  | ZM06
73 | KIPP10 | 10LCA10CP101 | CONDENSATE EXTRACTION PUMP DISCHARGE PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313297 |  |  | ZM06
74 | KIPP10 | 10LCA10CP102 | GLAND STEAM CONDENSER OUTLET PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313298 |  |  | ZM06
75 | KIPP10 | 10LCA10CP103 | CONDENSATE EXTRACTION PUMP DISCHARGE PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313310 |  |  | ZM06
76 | KIPP10 | 10LCA11CP101 | CEP-A DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313294 |  |  | ZM06
77 | KIPP10 | 10LCA12CP101 | CEP-B DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313295 |  |  | ZM06
78 | KIPP10 | 10LCA13CP101 | CEP-C DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313296 |  |  | ZM06
79 | KIPP10 | 10LCA20CF101 | DEAERATOR & FW STORAGE TANK INLET FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313069 |  |  | ZM06
80 | KIPP10 | 10MAA10CP001 | P UPSTR HPT BLADING |  | -1.013 | 275.789 | -1 | 150 | Bar | ROSEMOUNT | 3051 PT | 9834864 |  |  | ZM06
81 | KIPP10 | 10MAB10CP001 | P UPSTR IPT BLADING |  | -137.89 | 137.89 | -1 | 40 | Bar | ROSEMOUNT | 3051 PT | 9834862 |  |  | ZM06
82 | KIPP10 | 10MAB10CP002 | P UPSTR IPT BLADING |  | -137.89 | 137.89 | -1 | 40 | Bar | ROSEMOUNT | 3051 PT | 9834863 |  |  | ZM06
83 | KIPP10 | 10MAC01CP021 | LP TUR.UPER STR.CROSS PIPE PRESSURE |  | -20.684 | 20.684 | -1 | 8 | Bar | ROSEMOUNT | 3051 PT | 9834860 |  |  | ZM06
84 | KIPP10 | 10MAC01CP022 | LP TUR.UPER STR.CROSS PIPE PRESSURE |  | -20.684 | 20.684 | -1 | 8 | Bar | ROSEMOUNT | 3051 PT | 9834861 |  |  | ZM06
85 | KIPP10 | 10MAC10CP031 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861934 |  |  | ZM06
86 | KIPP10 | 10MAC10CP032 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861935 |  |  | ZM06
87 | KIPP10 | 10MAC10CP033 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861936 |  |  | ZM06
88 | KIPP10 | 10MAV40CP003 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843509 |  |  | ZM06
89 | KIPP10 | 10MAV40CP004 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843508 |  |  | ZM06
90 | KIPP10 | 10MAV40CP005 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843510 |  |  | ZM06
91 | KIPP10 | 10MAW02CP001 | GLAND STEAM LINE PT |  | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313309 |  |  | ZM06
92 | KIPP10 | 10MAW15CP001 | GLAND STEAM SEALING SYSTEM PRESSURE |  | -2486.4 | 2486.4 | -150 | 350 | mBar | ROSEMOUNT | 3051 PT | 9834859 |  |  | ZM06
93 | KIPP10 | 10MAX11CP031 | P HYDR HEADER |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843512 |  |  | ZM06
94 | KIPP10 | 10MAX44CP001 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843513 |  |  | ZM06
95 | KIPP10 | 10MAX44CP002 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843511 |  |  | ZM06
96 | KIPP10 | 10MAX44CP003 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843514 |  |  | ZM06
97 | KIPP10 | 10MKA13CP111 | GEN.AIR BLOWER FILTER PRESSURE |  | -1013.2 | 2068.4 | -50 | 0 | mBar | ROSEMOUNT | 2088 PT | 9917083 |  |  | ZM06
98 | KIPP10 | 10MKA13CP112 | GEN.AIR BLOWER AFTER FAN PRESSURE |  | -1013.2 | 2068.4 | 0 | 400 | mBar | ROSEMOUNT | 2088 PT | 9917081 |  |  | ZM06
99 | KIPP10 | 10MKA13CP113 | GEN.AIR BLOWER AFTER FAN PRESSURE |  | -1013.2 | 2068.4 | 0 | 400 | mBar | ROSEMOUNT | 2088 PT | 9917082 |  |  | ZM06
100 | KIPP11 | 11EKG40CP101 | FG PERFORMANCE HEATER SKID OUTLET PRESS |  | -1 | 100 | 0 | 61 | Bar | YOKOGAWA | EJA530E | 91S313313 |  |  | ZM06
101 | KIPP11 | 11HAC22CF002 | LP FW FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214472 |  |  | ZM06 |  |  | 11LAB46GH101
102 | KIPP11 | 11HAC22CF003 | LP FW FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214473 |  |  | ZM06 |  |  | 11LAB46GH101
103 | KIPP11 | 11HAC25CF002 | IP DRUM FW FLOW A | 2026-04-01 | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214462 |  |  | ZM06 |  |  | 11HAC25GH101
104 | KIPP11 | 11HAC25CF003 | IP DRUM FW FLOW B | 2026-04-01 | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214467 |  |  | ZM06 |  |  | 11HAC25GH101
105 | KIPP11 | 11HAC25CP001 | IP ECO O/L PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051TG | 210426 |  |  | ZM06 |  |  | 11HAC25GH101
106 | KIPP11 | 11HAC58CF002 | HP ECO O/L FT 1 | 2026-04-06 | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214452 |  |  | ZM06 |  |  | 11HAC58GH101
107 | KIPP11 | 11HAC58CF003 | HP ECO O/L FT 2 | 2026-04-06 | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214453 |  |  | ZM06 |  |  | 11HAC58GH101
108 | KIPP11 | 11HAC58CP001 | HP ECO O/L PT | 2026-04-06 | 0 | 689.7 | 0 | 300 | Bar | ROSEMOUNT | 2050 TG | 210420 |  |  | ZM06 |  |  | 11HAC58GH101
109 | KIPP11 | 11HAD10CL001 | LP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576009 |  |  | ZM06 |  |  | 11HAC25GH101
110 | KIPP11 | 11HAD10CL002 | LP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576010 |  |  | ZM06 |  |  | 11HAD50GH102
111 | KIPP11 | 11HAD10CL003 | LP DRUM LT 3 | 3.04.2026 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576011 |  |  | ZM06 |  |  | 11HAD50GH102
112 | KIPP11 | 11HAD10CP001 | LP DRUM PT 1 | 2026-04-06 | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576027 |  |  | ZM06 |  |  | 11HAD30GH101
113 | KIPP11 | 11HAD10CP002 | LP DRUM PT 2 | 2026-04-06 | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576028 |  |  | ZM06 |  |  | 11HAD30GH101
114 | KIPP11 | 11HAD10CP003 | LP DRUM PT 3 | 2026-04-06 | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576029 |  |  | ZM06 |  |  | 11HAD30GH101
115 | KIPP11 | 11HAD30CL001 | IP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576006 |  |  | ZM06 |  |  | 11HAC25GH101
116 | KIPP11 | 11HAD30CL002 | IP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576007 |  |  | ZM06 |  |  | 11HAD50GH102
117 | KIPP11 | 11HAD30CL003 | IP DRUM LT 3 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576008 |  |  | ZM06 |  |  | 11HAD50GH102
118 | KIPP11 | 11HAD30CP001 | IP DRUM PT 1 | 2026-04-03 | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575997 |  |  | ZM06 |  |  | 11HAD30GH101
119 | KIPP11 | 11HAD30CP002 | IP DRUM PT 2 | 2026-04-03 | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575998 |  |  | ZM06 |  |  | 11HAD30GH101
120 | KIPP11 | 11HAD30CP003 | IP DRUM PT 3 | 2026-04-03 | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575999 |  |  | ZM06 |  |  | 11HAD30GH101
121 | KIPP11 | 11HAD50CL001 | HP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576004 |  |  | ZM06 |  |  | 11HAC25GH101
122 | KIPP11 | 11HAD50CL002 | HP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576003 |  |  | ZM06 |  |  | 11HAD50GH102
123 | KIPP11 | 11HAD50CL003 | HP DRUM LT 3 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576005 |  |  | ZM06 |  |  | 11HAD50GH102
124 | KIPP11 | 11HAD50CP001 | HP DRUM PT 1 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575991 |  |  | ZM06 |  |  | 11HAD50GH101
125 | KIPP11 | 11HAD50CP002 | HP DRUM PT 2 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575992 |  |  | ZM06 |  |  | 11HAD50GH101
126 | KIPP11 | 11HAD50CP003 | HP DRUM PT 3 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575993 |  |  | ZM06 |  |  | 11HAD50GH101
127 | KIPP11 | 11LAB20CF101 | HP STEAM BYPASS SPRAYAY WATER FT |  | -6350 | 6350 | 0 | 6300 | mmH2O | ROSEMOUNT | 2051 PT | 214447 |  |  | ZM06
128 | KIPP11 | 11LAB31CF101 | FEED WATER FROM CONDENSATE PREHEATER FT | 2026-04-06 | -10197.2 | 10197.2 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313068 |  |  | ZM06 |  |  | 10LAB10GH101
129 | KIPP11 | 11LAB46CP001 | IP/LP FW PT | 2026-04-02 | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051 PT | 210430 |  |  | ZM06 |  |  | 11LAB46GH101
130 | KIPP11 | 11LAB90CP001 | FEED WATER TO GT OTC STRAINER PDT | 2026-04-06 | -5 | 5 | 0 | 2 | Bar | YOKOGAWA | EJA110E | 91S313545 |  |  | ZM06
131 | KIPP11 | 11LAB91CF101 | FW LP OTC FITCA | 2026-04-06 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816770 |  |  | ZM06
132 | KIPP11 | 11LAB91CF102 | FW LP OTC FITCA | 2026-04-06 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816771 |  |  | ZM06
133 | KIPP11 | 11LAB92CF101 | FW HP OTC FITCA | 2026-04-06 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816772 |  |  | ZM06
134 | KIPP11 | 11LAB92CF102 | FW HP OTC FITCA | 2026-04-06 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816773 |  |  | ZM06
135 | KIPP11 | 11LAB96CP001 | HP FW PT | 2026-04-02 | 0 | 289.3 | 0 | 300 | Bar | ROSEMOUNT | 2051 PT | 210424 |  |  | ZM06 |  |  | 11LAB96GH101
136 | KIPP11 | 11LAE50CF002 | HP DESUPERHEATER SPRAY FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214454 |  |  | ZM06 |  |  | 11LAE50GH101
137 | KIPP11 | 11LAE50CF003 | HP DESUPERHEATER SPRAY FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214455 |  |  | ZM06 |  |  | 11LAE50GH101
138 | KIPP11 | 11LAF40CF002 | RH DESUPERHEATER SPRAY FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214468 |  |  | ZM06 |  |  | 11LAB46GH101
139 | KIPP11 | 11LAF40CF003 | RH DESUPERHEATER SPRAY FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214469 |  |  | ZM06 |  |  | 11LAB46GH101
140 | KIPP11 | 11LBA00CP101 | HP STEAM PRESSURE | 2026-03-17 | -1 | 500 | 0 | 151 | Bar | YOKOGAWA | EJA530E | 91S313315 |  |  | ZM06 |  |  |  | Set: 2,2 - Reset: 1,99
141 | KIPP11 | 11LBA10CF002 | LP STEAM O/L FT 1 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214474 |  |  | ZM06 |  |  | 11LAB96GH101
142 | KIPP11 | 11LBA10CF003 | LP STEAM O/L FT 2 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214475 |  |  | ZM06 |  |  | 11LAB96GH101
143 | KIPP11 | 11LBA10CP001 | LP STEAM PRESSURE | 2026-03-24 | -1 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 210437 |  |  | ZM06 |  |  | 11LAB96GH101
144 | KIPP11 | 11LBA20CP101 | HP BYPASS VALVE OUTLET PRESSURE A | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313282 |  |  | ZM06
145 | KIPP11 | 11LBA20CP102 | HP BYPASS VALVE OUTLET PRESSURE B | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313283 |  |  | ZM06
146 | KIPP11 | 11LBA30CF002 | IP STEAM O/L FT 1 | 2026-04-06 | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214470 |  |  | ZM06 |  |  | 11LBA30GH101
147 | KIPP11 | 11LBA30CF003 | IP STEAM O/L FT 2 | 2026-04-06 | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214471 |  |  | ZM06 |  |  | 11LBA30GH101
148 | KIPP11 | 11LBA30CP001 | IP STEAM O/L PT | 2026-04-06 | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210431 | [5 empty] | 11LBA30GH101
149 | KIPP11 | 11LBA31CP101 | LP STEAM PT | 2026-03-24 | -1 | 20 | 0 | 10 | Bar | YOKOGAWA | EJA530E | 91S313226
150 | KIPP11 | 11LBA40CP101 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313227
151 | KIPP11 | 11LBA40CP102 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313228
152 | KIPP11 | 11LBA50CF002 | HP STEAM O/L FT 1 | 2026-04-02 | -2486 | 2486 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214456 |  |  | ZM06 |  |  | 11LBC00GH101
153 | KIPP11 | 11LBA50CF003 | HP STEAM O/L FT 2 | 2026-04-02 | -2486 | 2486 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214457 |  |  | ZM06 |  |  | 11LBC00GH101
154 | KIPP11 | 11LBA50CP001 | HP STEAM PT | 2026-04-02 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 210425 |  |  | ZM06
155 | KIPP11 | 11LBB00CP101 | HOT REHEAT STEAM PT | 2026-03-17 | -1 | 100 | 0 | 50 | Bar | YOKOGAWA | EJA530E | 91S313213
156 | KIPP11 | 11LBB20CP101 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313222
157 | KIPP11 | 11LBB20CP102 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313223 |  |  | ZM06
158 | KIPP11 | 11LBB40CP001 | HOT REHEAT STEAM PT | 2026-04-02 | -1.01 | 275.79 | 0 | 50 | Bar | ROSEMOUNT | 2051 PT | 210432 |  |  | ZM06 |  |  | 11LBA30GH101
159 | KIPP11 | 11LBC00CF101 | COLD REHEAT STEAM FLOW A | 2026-04-02 | -10197.2 | 10197.2 | 0 | 4756.2 | mmH2O | YOKOGAWA | EJA110E | 91S313071 |  |  | ZM06 |  |  | 11LBC00GH101
160 | KIPP11 | 11LBC00CF102 | COLD REHEAT STEAM FLOW B | 2026-04-02 | -10197.2 | 10197.2 | 0 | 4756.2 | mmH2O | YOKOGAWA | EJA110E | 91S313072 |  |  | ZM06 |  |  | 11LBC00GH101
161 | KIPP11 | 11LBC00CP101 | COLD REHEAT STEAM PRESSURE | 2026-04-02 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313287 |  |  | ZM06 |  |  | 11LBC00GH101
162 | KIPP11 | 11LBC30CP001 | COLD REHEAT STEAM PT | 2026-04-06 | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210433 |  |  | ZM06 |  |  | 11HAC58GH101
163 | KIPP11 | 11LBG91CP001 | GT OTC OUT STEAM LINE PT-1 | 2026-04-02 | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S313324 |  |  | ZM06
164 | KIPP11 | 11LBG91CP002 | GT OTC OUT STEAM LINE PT-2 | 2026-04-02 | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S313326 |  |  | ZM06
165 | KIPP11 | 11LCA20CF101 | LP STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313062 |  |  | ZM06
166 | KIPP11 | 11LCA21CF101 | HOT REHEAT STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313060 |  |  | ZM06
167 | KIPP11 | 11MBA30CP001 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824805 |  |  | ZM06
168 | KIPP11 | 11MBA30CP003 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824806 |  |  | ZM06
169 | KIPP11 | 11MBA30CP004 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824807 |  |  | ZM06
170 | KIPP11 | 11MBA80CP051 | GT AFT COMPRESSOR 1H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825256 |  |  | ZM06
171 | KIPP11 | 11MBA80CP052 | GT AFT COMPRESSOR 4H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825257 |  |  | ZM06
172 | KIPP11 | 11MBA80CP054 | P AFT COMPRESSOR 8H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CD | 9825258 |  |  | ZM06
173 | KIPP11 | 11MBE41CP013 | GT H/F WATER PUMP SUCTION FILTER PDT |  | 0 | 0 | -1000 | 2200 | mBar | ROSEMOUNT | 2088TG | 2753518 |  |  | ZM06
174 | KIPP11 | 11MBE41CP121 | GT H/F WATER PUMP-1 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210595 |  |  | ZM06
175 | KIPP11 | 11MBE41CP122 | GT H/F WATER PUMP-2 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210445 |  |  | ZM06
176 | KIPP11 | 11MBE41CP123 | GT H/F WATER PUMP-3 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210429 |  |  | ZM06
177 | KIPP11 | 11MBE41CP124 | GT H/F WATER PUMP-4 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210446 |  |  | ZM06
178 | KIPP11 | 11MBE41CP141 | GT H/F WATER PUMP-1 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631493 |  |  | ZM06
179 | KIPP11 | 11MBE41CP142 | GT H/F WATER PUMP-2 DISCHARGE PT |  | -14.7 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 607375 |  |  | ZM06
180 | KIPP11 | 1: 11MBE41CP143; 2: GT H/F WATER PUMP-3 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631492
181 | KIPP11 | 11MBE41CP144 | GT H/F WATER PUMP-4 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631494 |  |  | ZM06
182 | KIPP11 | 11MBH20CP007 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825262 |  |  | ZM06
183 | KIPP11 | 11MBH20CP008 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825263 |  |  | ZM06
184 | KIPP11 | 11MBH20CP009 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825264 |  |  | ZM06
185 | KIPP11 | 11MBH30CL001 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-19 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313549 |  |  | ZM06
186 | KIPP11 | 11MBH30CL002 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-19 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313550 |  |  | ZM06
187 | KIPP11 | 11MBH30CP003 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 PT | 9825259 |  |  | ZM06
188 | KIPP11 | 11MBH30CP004 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 PT | 9825260 |  |  | ZM06
189 | KIPP11 | 11MBH30CP005 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825261 |  |  | ZM06
190 | KIPP11 | 11MBH30CP015 | PRESSURE DIFF ACROSS LP AIR COOLER | 2026-01-19 | -20.684 | 20.684 | 0 | 4 | Bar | ROSEMOUNT | 3051 PT | 9824811 |  |  | ZM06
191 | KIPP11 | 11MBH30CP020 | P QUENSCH WATER TO LP COOLER | 2026-01-20 | -137.89 | 137.89 | 0 | 30 | Bar | ROSEMOUNT | 3051 PT | 9825287 |  |  | ZM06
192 | KIPP11 | 11MBH30CP021 | GT SEV COMBUSTOR LINER/KA01 PDT | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825276 |  |  | ZM06
193 | KIPP11 | 11MBH30CP022 | P DIFF SEV COMBUSTOR LINER/KA01 | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825274 |  |  | ZM06
194 | KIPP11 | 11MBH30CP023 | P DIFF SEV COMBUSTOR LINER/KA01 | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825275 |  |  | ZM06
195 | KIPP11 | 11MBH40CL001 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-20 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313547 |  |  | ZM06
196 | KIPP11 | 11MBH40CL002 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-20 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313548 |  |  | ZM06
197 | KIPP11 | 11MBH40CP015 | DP HP OTC | 2026-01-20 | -621.6 | 621.6 | 0 | 500 | mBar | ROSEMOUNT | 3051 PT | 9825290 |  |  | ZM06
198 | KIPP11 | 11MBH41CP102 | PRESSURE AFTER BLOW-OFF BYPASS VALVE | 2026-01-20 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CD | 9855800 |  |  | ZM06
199 | KIPP11 | 11MBH41CP103 | DP FLOW MEASUREMENT | 2026-01-20 | -20.684 | 20.684 | 0 | 10 | Bar | ROSEMOUNT | 3051CD | 9855803 |  |  | ZM06
200 | KIPP11 | 11MBH52CP001 | EXHAUST BEARING FAN 1 PDI | 2026-01-20 | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891371 |  |  | ZM06
201 | KIPP11 | 11MBH52CP002 | EXHAUST BEARING FAN 2 PDI | 2026-01-20 | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891372 |  |  | ZM06
202 | KIPP11 | 11MBH60CP001 | DP CMAS FAN 1 | 2026-01-20 | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891369
203 | KIPP11 | 11MBH60CP002 | DP CMAS FAN 2 | 2026-01-20 | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891370 |  |  | ZM06
204 | KIPP11 | 11MBH80CP011 | DIFFERENTIAL PRESSURE EV COMBUSTOR | 2026-01-20 | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825280 |  |  | ZM06
205 | KIPP11 | 11MBH80CP012 | DIFFERENTIAL PRESSURE EV COMBUSTOR | 2026-01-20 | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825281 |  |  | ZM06
206 | KIPP11 | 11MBH90CP001 | PRESSURE BEFORE ANTI-ICING CONTROL VALVE | 2026-01-21 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914214 |  |  | ZM06
207 | KIPP11 | 11MBH90CP004 | DP OVER ANTI ICING CV | 2026-01-21 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914216 |  |  | ZM06
208 | KIPP11 | 11MBL01CP011 | DP AIR INTK FLTR TOT | 2026-01-21 | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 9844811 |  |  | ZM06
209 | KIPP11 | 11MBL01CP012 | DP AIR INTK FLTR TOT | 2026-01-21 | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 9844812 |  |  | ZM06
210 | KIPP11 | 11MBL51CP001 | DP PRE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844805 |  |  | ZM06
211 | KIPP11 | 11MBL51CP002 | DP FINE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844806 |  |  | ZM06
212 | KIPP11 | 11MBL51CP012 | DP FINE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844807 |  |  | ZM06
213 | KIPP11 | 11MBL61CP010 | EVAP COOLER PUMP AFTER PRESSURE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051CD | 9852954 |  |  | ZM06
214 | KIPP11 | 11MBP01CP003 | FUEL GAS FILTER DP | 2026-01-21 | -2.4864 | 2.4864 | 0 | 1.5 | Bar | ROSEMOUNT | 3051 PT | 9789262 |  |  | ZM06
215 | KIPP11 | 11MBP05CP102 | EV FUEL GAS FLOW PT | 2026-01-21 | 0 | 55.16 | 0 | 55 | Bar | ROSEMOUNT | 3051 PT | 9846441 |  |  | ZM06 |  |  |  | Atm. Basıncı 0,935 Bar
216 | KIPP11 | 11MBP41CP001 | P AFT TRIP SOV EV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782024 |  |  | ZM06
217 | KIPP11 | 11MBP41CP004 | DP CV EV STG2 | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782030 |  |  | ZM06
218 | KIPP11 | 11MBP41CP006 | P AFT CV FGAS EV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782025 |  |  | ZM06
219 | KIPP11 | 11MBP42CP001 | P BEF FGAS TRIP SOV SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782026 |  |  | ZM06
220 | KIPP11 | 11MBP42CP004 | DP CV FGAS SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782031 |  |  | ZM06
221 | KIPP11 | 11MBP42CP006 | P AFT CV FGAS SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782027 |  |  | ZM06
222 | KIPP11 | 11MBP43CP001 | P BFR CV EV STG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782028 |  |  | ZM06
223 | KIPP11 | 11MBP43CP004 | DP CV EVSTG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782032 |  |  | ZM06
224 | KIPP11 | 11MBP43CP006 | P AFT CV EV STG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782029 |  |  | ZM06
225 | KIPP11 | 11MBV10CP001 | PRESSURE LUBE OIL TANK | 2026-01-22 | -621.6 | 621.6 | 0 | 60 | mBar | ROSEMOUNT | 3051 PT | 9781969 |  |  | ZM06
226 | KIPP11 | 11MBV21CP001 | P AFT LUBE OIL PMP 1 | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791817 |  |  | ZM06
227 | KIPP11 | 11MBV21CP002 | P AFT LUBE OIL PMP 2 | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791818 |  |  | ZM06
228 | KIPP11 | 11MBV21CP003 | LUBE OIL FILTER DP | 2026-01-22 | -2.4864 | 2.4864 | -2.5 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9781970 |  |  | ZM06
229 | KIPP11 | 11MBV22CP001 | EMERGENCY LUBE OIL PUMP AFTER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791819 |  |  | ZM06
230 | KIPP11 | 11MBV40CP001 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791820 |  |  | ZM06
231 | KIPP11 | 11MBV40CP002 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791821 |  |  | ZM06
232 | KIPP11 | 11MBV40CP003 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791822 |  |  | ZM06
233 | KIPP11 | 11MBV40CP006 | P LUBE OIL HEADER 6 ( PRESSURE SWITCH ) | 2026-01-22 | 0 | 10 | - | 2.11 | Bar | TRAFOG | Switch | - |  |  | ZM06
234 | KIPP11 | 11MBX21CP001 | P AFT PWR OIL PMP 2 | 2026-01-22 | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791823 |  |  | ZM06
235 | KIPP11 | 11MBX21CP002 | P AFT PWR OIL PMP 1 | 2026-01-22 | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791824 |  |  | ZM06
236 | KIPP11 | 11MBX21CP010 | GT P/O TWIN FILTER PDT | 2026-01-22 | -20.684 | 20.684 | -2 | 8 | Bar | ROSEMOUNT | 3051CD | 9782033 |  |  | ZM06
237 | KIPP11 | 11MBX42CP001 | P HYDR SAFETY SYS | 2026-01-22 | -137.89 | 137.89 | 0 | 60 | Bar | ROSEMOUNT | 3051 PT | 9782034 |  |  | ZM06
238 | KIPP12 | 12EKG40CP101 | FG PERFORMANCE HEATER SKID OUTLET PRESS |  | -1 | 100 | 0 | 61 | Bar | YOKOGAWA | EJA530E | 91S313314 |  |  | ZM06
239 | KIPP12 | 12HAC22CF002 | LP FW FT 1 |  | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214484 |  |  | ZM06 |  |  | 12LAB46GH101
240 | KIPP12 | 12HAC22CF003 | LP FW FT 2 |  | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214485 |  |  | ZM06 |  |  | 12LAB46GH101
241 | KIPP12 | 12HAC25CF002 | IP DRUM FW FLOW A |  | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214478 |  |  | ZM06 |  |  | 12HAC25GH101
242 | KIPP12 | 12HAC25CF003 | IP DRUM FW FLOW B |  | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214479 |  |  | ZM06 |  |  | 12HAC25GH101
243 | KIPP12 | 12HAC25CP001 | IP ECO O/L PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051TG | 210444 |  |  | ZM06 |  |  | 12HAC25GH101
244 | KIPP12 | 12HAC58CF002 | HP ECO O/L FT 1 |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214463 |  |  | ZM06 |  |  | 12HAC58GH101
245 | KIPP12 | 12HAC58CF003 | HP ECO O/L FT 2 |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214464 |  |  | ZM06 |  |  | 12HAC58GH101
246 | KIPP12 | 12HAC58CP001 | HP ECO O/L PT |  | 0 | 689.7 | 0 | 300 | Bar | ROSEMOUNT | 2050TG | 210438 |  |  | ZM06 |  |  | 12HAC58GH101
247 | KIPP12 | 12HAD10CL001 | LP DRUM LT 1 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576021 |  |  | ZM06 |  |  | 12HAC25GH101
248 | KIPP12 | 12HAD10CL002 | LP DRUM LT 2 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576022 |  |  | ZM06 |  |  | 12HAD50GH102
249 | KIPP12 | 12HAD10CL003 | LP DRUM LT 3 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576023 |  |  | ZM06 |  |  | 12HAD50GH102
250 | KIPP12 | 12HAD10CP001 | LP DRUM PT 1 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576030 |  |  | ZM06 |  |  | 12HAD30GH101
251 | KIPP12 | 12HAD10CP002 | LP DRUM PT 2 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576031 |  |  | ZM06 |  |  | 12HAD30GH101
252 | KIPP12 | 12HAD10CP003 | LP DRUM PT 3 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576032 |  |  | ZM06 |  |  | 12HAD30GH101
253 | KIPP12 | 12HAD30CL001 | IP DRUM LT 1 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576018 |  |  | ZM06 |  |  | 12HAC25GH101
254 | KIPP12 | 12HAD30CL002 | IP DRUM LT 2 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576019 |  |  | ZM06 |  |  | 12HAD50GH102
255 | KIPP12 | 12HAD30CL003 | IP DRUM LT 3 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576020 |  |  | ZM06 |  |  | 12HAD50GH102
256 | KIPP12 | 12HAD30CP001 | IP DRUM PT 1 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576000 |  |  | ZM06 |  |  | 12HAD30GH101
257 | KIPP12 | 12HAD30CP002 | IP DRUM PT 2 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576001 |  |  | ZM06 |  |  | 12HAD30GH101
258 | KIPP12 | 12HAD30CP003 | IP DRUM PT 3 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576002 |  |  | ZM06 |  |  | 12HAD30GH101
259 | KIPP12 | 12HAD50CL001 | HP DRUM LT 1 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576015 |  |  | ZM06 |  |  | 12HAC25GH101
260 | KIPP12 | 12HAD50CL002 | HP DRUM LT 2 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576016 |  |  | ZM06 |  |  | 12HAD50GH102
261 | KIPP12 | 12HAD50CL003 | HP DRUM LT 3 |  | -6350 | 6350 | -33 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576017 |  |  | ZM06 |  |  | 12HAD50GH102
262 | KIPP12 | 12HAD50CP001 | HP DRUM PT 1 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575994 |  |  | ZM06 |  |  | 12HAD50GH101
263 | KIPP12 | 12HAD50CP002 | HP DRUM PT 2 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575995 |  |  | ZM06 |  |  | 12HAD50GH101
264 | KIPP12 | 12HAD50CP003 | HP DRUM PT 3 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575996 |  |  | ZM06 |  |  | 12HAD50GH101
265 | KIPP12 | 12LAB20CF101 | HP STEAM BYPASS SPRAYAY WATER FT |  | -6350 | 6350 | 0 | 6300 | mmH2O | ROSEMOUNT | 2051 PT | 214441 |  |  | ZM06
266 | KIPP12 | 12LAB31CF101 | FW FROM CONDENSATE PREHEATER FT |  | -10197.2 | 10197.2 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313067 |  |  | ZM06 |  |  | 10LAB10GH101
267 | KIPP12 | 12LAB46CP001 | IP/LP FW PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051 PT | 210448 |  |  | ZM06 |  |  | 12LAB46GH101
268 | KIPP12 | 12LAB96CP001 | HP FW PT |  | 0 | 689.5 | 0 | 300 | Bar | ROSEMOUNT | 2051 PT | 210442 |  |  | ZM06 |  |  | 12LAB96GH101
269 | KIPP12 | 12LAE50CF002 | HP DESUPERHEATER SPRAY FT 1 |  | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214465 |  |  | ZM06 |  |  | 12LAE50GH101
270 | KIPP12 | 12LAE50CF003 | HP DESUPERHEATER SPRAY FT 2 |  | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214466 |  |  | ZM06 |  |  | 12LAE50GH101
271 | KIPP12 | 12LAF40CF002 | RH DESUPERHEATER SPRAY FT 1 |  | -635 | 635 | 0 | 322 | mbar | ROSEMOUNT | 2051 PT | 214480 |  |  | ZM06 |  |  | 12LAB46GH101
272 | KIPP12 | 12LAF40CF003 | RH DESUPERHEATER SPRAY FT 2 |  | -635 | 635 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214481 |  |  | ZM06 |  |  | 12LAB46GH101
273 | KIPP12 | 12LBA00CP101 | HIGH PRESSURE STEAM PRESSURE | 2026-03-17 | -1 | 500 | 0 | 151 | Bar | ROSEMOUNT | EJA530E | 91S313316 |  |  | ZM06
274 | KIPP12 | 12LBA10CF002 | LP STEAM O/L FT 1 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214635 |  |  | ZM06 |  |  | 12LAB96GH101
275 | KIPP12 | 12LBA10CF003 | LP STEAM O/L FT 2 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214636 |  |  | ZM06 |  |  | 12LAB96GH101
276 | KIPP12 | 12LBA10CP001 | LP STEAM PT | 2026-03-24 | -1 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 210454 |  |  | ZM06 |  |  | 12LAB96GH101
277 | KIPP12 | 12LBA20CP101 | HP BYPASS VALVE OUTLET PRESSURE A | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313284 |  |  | ZM06
278 | KIPP12 | 12LBA20CP102 | HP BYPASS VALVE OUTLET PRESSURE B | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313285 |  |  | ZM06
279 | KIPP12 | 12LBA30CF002 | IP STEAM O/L FT 1 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214482 |  |  | ZM06 |  |  | 12LBA30GH101
280 | KIPP12 | 12LBA30CF003 | IP STEAM O/L FT 2 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214483 |  |  | ZM06 |  |  | 12LBA30GH101
281 | KIPP12 | 12LBA30CP001 | IP STEAM O/L PT |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210449 |  |  | ZM06 |  |  | 12LBA30GH101
282 | KIPP12 | 12LBA31CP101 | LP STEAM PT | 2026-03-24 | -1 | 20 | 0 | 10 | Bar | YOKOGAWA | EJA530E | 91S313229 |  |  | ZM06
283 | KIPP12 | 12LBA40CP101 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313230 |  |  | ZM06
284 | KIPP12 | 12LBA40CP102 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313231 |  |  | ZM06
285 | KIPP12 | 12LBA50CF002 | HP STEAM O/L FT 1 |  | -2468 | 2468 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214476 |  |  | ZM06 |  |  | 12LBC00GH101
286 | KIPP12 | 12LBA50CF003 | HP STEAM O/L FT 2 |  | -2468 | 2468 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214477 |  |  | ZM06 |  |  | 12LBC00GH101
287 | KIPP12 | 12LBA50CP001 | HP STEAM PT |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 210443 |  |  | ZM06
288 | KIPP12 | 12LBB00CP101 | HOT REHEAT STEAM PT | 2026-03-17 | -1 | 500 | 0 | 50 | Bar | YOKOGAWA | EJA530E | 91S313215 |  |  | ZM06
289 | KIPP12 | 12LBB20CP101 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313224 |  |  | ZM06
290 | KIPP12 | 12LBB20CP102 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313225 |  |  | ZM06
291 | KIPP12 | 12LBB40CP001 | RH STEAM PT |  | -1.01 | 275.79 | 0 | 50 | Bar | ROSEMOUNT | 2051 PT | 210450 |  |  | ZM06 |  |  | 12LBA30GH101
292 | KIPP12 | 12LBC00CF101 | COLD REHEAT STEAM FLOW A |  | -10197.2 | 10197.2 | 0 | 2312 | mmH2O | YOKOGAWA | EJA110E | 91S313073 |  |  | ZM06 |  |  | 12LBC00GH101
293 | KIPP12 | 12LBC00CF102 | COLD REHEAT STEAM FLOW B |  | -10197.2 | 10197.2 | 0 | 2312 | mmH2O | YOKOGAWA | EJA110E | 91S313074 |  |  | ZM06 |  |  | 12LBC00GH101
294 | KIPP12 | 12LBC00CP101 | COLD REHEAT STEAM PRESSURE |  | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S213288 |  |  | ZM06 |  |  | 12LBC00GH101
295 | KIPP12 | 12LBC30CP001 | COLD REHEAT PRESSURE |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210451 |  |  | ZM06 |  |  | 12HAC58GH101
296 | KIPP12 | 12LBG91CP001 | GT OTC OUT STEAM LINE PT-1 |  | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S213325 |  |  | ZM06
297 | KIPP12 | 12LBG91CP002 | GT OTC OUT STEAM LINE PT-1 |  | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S213327 |  |  | ZM06
298 | KIPP12 | 12LCA20CF101 | LP STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313063 |  |  | ZM06
299 | KIPP12 | 12LCA21CF101 | HOT REHEAT STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313061 |  |  | ZM06
300 | KIPP12 | 12MBA30CP001 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824808 |  |  | ZM06
301 | KIPP12 | 12MBA30CP003 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824809 |  |  | ZM06
302 | KIPP12 | 12MBA30CP004 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824810 |  |  | ZM06
303 | KIPP12 | 12MBA80CP051 | GT AFT COMPRESSOR 1H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825265 |  |  | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
304 | KIPP12 | 12MBA80CP052 | GT AFT COMPRESSOR 4H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825266 |  |  | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
305 | KIPP12 | 12MBA80CP054 | P AFT COMPRESSOR 8H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 | 9825267 |  |  | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
306 | KIPP12 | 12MBE41CP013 | GT H/F WATER PUMP SUCTION FILTER PDT |  | 0 | 0 | -1000 | 2200 | mBar | ROSEMOUNT | 2088TG | 2753519 |  |  | ZM06
307 | KIPP12 | 1: 12MBE41CP121; 2: GT H/F WATER PUMP-1 SUCTION PT; 4: -14.7; 5: 800; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 210447
308 | KIPP12 | 1: 12MBE41CP122; 2: GT H/F WATER PUMP-2 SUCTION PT; 4: -14.7; 5: 4000; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 210453
309 | KIPP12 | 1: 12MBE41CP123; 2: GT H/F WATER PUMP-3 SUCTION PT; 4: -14.7; 5: 800; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 10195290
310 | KIPP12 | 1: 12MBE41CP124; 2: GT H/F WATER PUMP-4 SUCTION PT; 4: -14.7; 5: 4000; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 10195289
311 | KIPP12 | 1: 12MBE41CP141; 2: GT H/F WATER PUMP-1 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631491
312 | KIPP12 | 1: 12MBE41CP142; 2: GT H/F WATER PUMP-2 DISCHARGE PT; 4: -14.7; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631489
313 | KIPP12 | 1: 12MBE41CP143; 2: GT H/F WATER PUMP-3 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631490
314 | KIPP12 | 1: 12MBE41CP144; 2: GT H/F WATER PUMP-4 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631487
315 | KIPP12 | 12MBH20CP007 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825271 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
316 | KIPP12 | 12MBH20CP008 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825272 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
317 | KIPP12 | 12MBH20CP009 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825273 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
318 | KIPP12 | 1: 12MBH30CL001; 2: LP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313553
319 | KIPP12 | 1: 12MBH30CL002; 2: LP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313554
320 | KIPP12 | 12MBH30CP003 | P SEV COMBUSTOR PLENUM/KA01 |  | -137.89 | 137.89 | 0 | 25 | Bar | YOKOGAWA | 3051 | 9825268 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
321 | KIPP12 | 12MBH30CP004 | P SEV COMBUSTOR PLENUM/KA01 |  | 137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825269 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
322 | KIPP12 | 12MBH30CP005 | P SEV COMBUSTOR PLENUM/KA01 |  | 137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825270 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
323 | KIPP12 | 1: 12MBH30CP015; 2: PRESSURE DIFF ACROSS LP AIR COOLER; 4: -20.684; 5: 20.684; 6: 0; 7: 4; 8: Bar; 9: ROSEMOUNT; 10: 3051; 11: 9824812
324 | KIPP12 | 1: 12MBH30CP020; 2: P QUENSCH WATER TO LP COOLER; 4: 137.89; 5: 137.89; 6: 0; 7: 30; 8: Bar; 9: ROSEMOUNT; 10: 3051; 11: 9825289
325 | KIPP12 | 12MBH30CP021 | DP SEV COMBUSTOR LINER |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825279 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
326 | KIPP12 | 12MBH30CP022 | P DIFF SEV COMBUSTOR LINER/KA01 |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825277 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
327 | KIPP12 | 12MBH30CP023 | P DIFF SEV COMBUSTOR LINER/KA01 |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825278 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
328 | KIPP12 | 1: 12MBH40CL001; 2: HP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313551
329 | KIPP12 | 1: 12MBH40CL002; 2: HP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313552
330 | KIPP12 | 1: 12MBH40CP015; 2: DP HP OTC; 4: -621.6; 5: 621.6; 6: 0; 7: 500; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9825291
331 | KIPP12 | 1: 12MBH41CP102; 2: PRESSURE AFTER BLOW-OFF BYPASS VALVE; 4: -137.89; 5: 137.89; 6: 0; 7: 40; 8: Bar; 9: ROSEMOUNT; 10: 3051CD
332 | KIPP12 | 1: 12MBH41CP103; 2: DP FLOW MEASUREMENT; 4: -20.684; 5: 20.684; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 3051CD
333 | KIPP12 | 1: 12MBH52CP001; 2: EXHAUST BEARING FAN 1 PDI; 4: -621.6; 5: 621.6; 6: 0; 7: 400; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891375
334 | KIPP12 | 1: 12MBH52CP002; 2: EXHAUST BEARING FAN 2 PDI; 4: -621.6; 5: 621.6; 6: 0; 7: 400; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891376
335 | KIPP12 | 1: 12MBH60CP001; 2: DP CMAS FAN 1; 4: -621.6; 5: 621.6; 6: 0; 7: 50; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891373
336 | KIPP12 | 1: 12MBH60CP002; 2: DP CMAS FAN 2; 4: -621.6; 5: 621.6; 6: 0; 7: 50; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891374
337 | KIPP12 | 1: 12MBH80CP011; 2: DIFFERENTIAL PRESSURE EV COMBUSTOR; 4: -2.4864; 5: 2.4864; 6: 0; 7: 2.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9825282
338 | KIPP12 | 1: 12MBH80CP012; 2: DIFFERENTIAL PRESSURE EV COMBUSTOR; 4: -2.4864; 5: 2.4864; 6: 0; 7: 2.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9825283
339 | KIPP12 | 1: 12MBH90CP001; 2: PRESSURE BEFORE ANTI-ICING CONTROL VALVE; 4: -137.89; 5: 137.89; 6: 0; 7: 40; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9914215
340 | KIPP12 | 1: 12MBH90CP004; 2: DP OVER ANTI ICING CV; 4: -137.89; 5: 137.89; 6: 0; 7: 40; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9914217
341 | KIPP12 | 1: 12MBL01CP011; 2: DP AIR INTK FLTR TOT; 4: -621.6; 5: 621.6; 6: 0; 7: 3000; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 98426871
342 | KIPP12 | 1: 12MBL01CP012; 2: DP AIR INTK FLTR TOT; 4: -621.6; 5: 621.6; 6: 0; 7: 3000; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844814
343 | KIPP12 | 1: 12MBL51CP001; 2: DP PRE FLTR STAGE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844808
344 | KIPP12 | 1: 12MBL51CP002; 2: DP FINE FLTR STAGE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844809
345 | KIPP12 | 1: 12MBL51CP012; 2: DP FINE FLTR STAGE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844810
346 | KIPP12 | 1: 12MBL61CP010; 2: EVAP COOLER PUMP AFTER PRESSURE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9852955
347 | KIPP12 | 1: 12MBP01CP003; 2: FUEL GAS FILTER DP; 4: -2.4864; 5: 2.4864; 6: 0; 7: 1.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9789263
348 | KIPP12 | 12MBP05CP102 | EV FUEL GAS FLOW PT |  | 0 | 55.16 | 0 | 55 | Bar | ROSEMOUNT | 3051 PT | 9846442 | [6 empty] | Atm. Basıncı 0,935 Bar
349 | KIPP12 | 1: 12MBP41CP001; 2: P AFT TRIP SOV EV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782037
350 | KIPP12 | 1: 12MBP41CP004; 2: DP CV EV STG2; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782043
351 | KIPP12 | 1: 12MBP41CP006; 2: P AFT CV FGAS EV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782038
352 | KIPP12 | 1: 12MBP42CP001; 2: P BEF FGAS TRIP SOV SEV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782039
353 | KIPP12 | 1: 12MBP42CP004; 2: DP CV FGAS SEV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782044
354 | KIPP12 | 1: 12MBP42CP006; 2: P AFT CV FGAS SEV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782040
355 | KIPP12 | 1: 12MBP43CP001; 2: P BFR CV EV STG1 FGAS; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782041
356 | KIPP12 | 1: 12MBP43CP004; 2: DP CV EVSTG1 FGAS; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782045
357 | KIPP12 | 1: 12MBP43CP006; 2: P AFT CV EV STG1 FGAS; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782042
358 | KIPP12 | 1: 12MBV10CP001; 2: PRESSURE LUBE OIL TANK; 4: -62.16; 5: 62.16; 6: 0; 7: 60; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782022
359 | KIPP12 | 1: 12MBV21CP001; 2: P AFT LUBE OIL PMP 1; 4: -1.013; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791825
360 | KIPP12 | 1: 12MBV21CP002; 2: P AFT LUBE OIL PMP 2; 4: -1.013; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791826
361 | KIPP12 | 1: 12MBV21CP003; 2: LUBE OIL FILTER DP; 4: -2.4864; 5: 2.4864; 6: -2.5; 7: 2.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782023
362 | KIPP12 | 1: 12MBV22CP001; 2: EMERGENCY LUBE OIL PUMP AFTER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791827
363 | KIPP12 | 1: 12MBV40CP001; 2: LUBE OIL HEADER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791828
364 | KIPP12 | 1: 12MBV40CP002; 2: LUBE OIL HEADER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791829
365 | KIPP12 | 1: 12MBV40CP003; 2: LUBE OIL HEADER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791830
366 | KIPP12 | 1: 12MBV40CP006; 2: P LUBE OIL HEADER 6 ( PRESSURE SWITCH ); 4: 0; 5: 10; 6: 1.99; 7: 2.2; 8: Bar; 9: Trafog; 10: Switch; 11: -
367 | KIPP12 | 1: 12MBX21CP001; 2: P AFT PWR OIL PMP 1; 4: -1.01; 5: 55.16; 6: 0; 7: 52; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791831
368 | KIPP12 | 1: 12MBX21CP002; 2: P AFT PWR OIL PMP 2; 4: -1.01; 5: 55.16; 6: 0; 7: 52; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791832
369 | KIPP12 | 1: 12MBX21CP010; 2: GT P/O TWIN FILTER PDT; 4: -20.684; 5: 20.684; 6: -2; 7: 8; 8: Bar; 9: ROSEMOUNT; 10: 3051CD; 11: 9782046
370 | KIPP12 | 1: 12MBX42CP001; 2: P HYDR SAFETY SYS; 4: -137.89; 5: 137.89; 6: 0; 7: 60; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782047
371 | KIPP12 | 1: 12LAB90CP001; 2: FEED WATER TO GT OTC STRAINER PDT; 4: -5; 5: 5; 6: 0; 7: 2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313546
372 | KIPP12 | 12LAB91CF101 | FW LP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816774
373 | KIPP12 | 12LAB91CF102 | FW LP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816937
374 | KIPP12 | 12LAB92CF101 | FW HP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816776
375 | KIPP12 | 12LAB92CF102 | FW HP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816777
376
377
378
379
380

## Reject List
No | Functional Loc. | Description | Start Date | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No. | Tx Status | SAP Ekipman Kodu | Order Type | SAP Status | Comments
| KIPP10MAA10CT031A | HP TURBINE EXHAUST THERMOCOUPLE |  | - | - | - | - | ᵒC | - | - | - | Waiting | 10296596 | ZM06 |  | Dublicate
| KIPP10MAA10CT031B | HP TURBINE EXHAUST THERMOCOUPLE |  | - | - | - | - | ᵒC | - | - | - | Waiting | 10296597 | ZM06 |  | Dublicate
| KIPP10MAW10CT001 | GLAND STEAM SEALING SYSTEM |  | - | - | - | - | ᵒC | - | - | - | Waiting | 10297154 | ZM06 |  | Dublicate
| KIPP10MAW10CT002 | GLAND STEAM SEALING SYSTEM |  | - | - | - | - | ᵒC | - | - | - | Waiting | 10297155 | ZM06 |  | Dublicate
| KIPP12MBP41CP100 | EV STG2 FUEL GAS PRESSURE MEASUREMENT |  | 0 | 275.79 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | - | Waiting | 10302853 | ZM06 |  | For Commissionnig
| KIPP12MBP43CP100 | EV STG1 FUEL GAS PRESSURE MEASUREMENT |  | 0 | 275.79 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | - | Waiting | 10302882 | ZM06 |  | For Commissionnig
| KIPP11MBP41CP100 | EV STG2 FUEL GAS PRESSURE MEASUREMENT |  | 0 | 275.79 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782036 | Waiting | 10300348 | ZM06 |  | For Commissionnig
| KIPP11MBP43CP100 | EV STG1 FUEL GAS PRESSURE MEASUREMENT |  | 0 | 275.79 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | - | Waiting | 10300377 | ZM06 |  | For Commissionnig

## Kalibrasyon Ekipmanları
1 | 2 | 3 | 4 | 5 | 6 | 7
A | Fluke 754 Multifunction Process Calibrator |  | Beamex Calibration Pressure Pump 0 - 700 Bar | - | Fluke 750P30 High Pressure Module 340 Bar
B | Fluke 754 Multifunction Process Calibrator |  | Beamex Calibration Pressure Pump 0 - 700 Bar | - | Fluke 750P07 Gage Pressure Module 35 Bar
C | Fluke 754 Multifunction Process Calibrator |  | Beamex Calibration Pressure Pump 0 - 20 Bar | - | Fluke 750P06 Gage Pressure Module 7 Bar
D | Fluke 754 Multifunction Process Calibrator |  | Beamex Calibration Pressure Pump 0 - 20 Bar | - | Fluke 750PD5 Dual Range Pressure Module -1+2 Bar
E | Beamex MC6 | - | Beamex Calibration Pressure Pump 0 - 700 Bar | - | EXTERNAL PRESSURE MODULE EXT 100M | -
F | Beamex MC6 | - | Beamex Calibration Pressure Pump 0 - 20 Bar | - | EXTERNAL PRESSURE MODULE EXT 250 | -

## PRINT
|  | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 10 | 11 | 15
No | Functional Location | Description | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No.
1 | 00GHC24CF101
2 | 10LAA00CP101
3 | 10LAA00CP102
4 | 10LAA00CP103
5 | 10LAB01CP102
6 | 10LAB02CP102
7 | 10LAB03CP102
8 | 10LAB06CP102
9 | 10LAB07CP102
10 | 10LAB08CP102
11 | 10LAB10CP101
12 | 10LAB10CP102
13 | 10LAB11CP101
14 | 10LAB12CP101
15 | 10LAB13CP101
16 | 10LAB24CF101
17 | 10LAB30CP101
18 | 10LAB30CP102
19 | 10LAB31CP101
20 | 10LAB32CP101
21 | 10LAB33CP101
22 | 10LCA01CP102
23 | 10LCA02CP102
24 | 10LCA03CP102
25 | 10LCA10CF101
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
No | Functional Location | Description | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
No | Functional Location | Description | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
No | Functional Location | Description | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## Tx Detail List (old)
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  |  | 15
No | Group | Functional Location | Description | Calibration Date | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No. | Tx Status | SAP Ekipman Kodu | Order Type | SAP Status | Full Model Number | Panel KKS | Comments
1 | KIPP00 | 00GHC01CP101 | DEMIN WATER PUMP-A SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313262 |  | 10291821 | ZM06
2 | KIPP00 | 00GHC01CP102 | DEMIN WATER PUMP-A SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313090 |  | 10291822 | ZM06
3 | KIPP00 | 00GHC02CP101 | DEMIN WATER PUMP-B SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313263 |  | 10295565 | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
4 | KIPP00 | 00GHC02CP102 | DEMIN WATER PUMP-B SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313091 |  | 10295566 | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
5 | KIPP00 | 00GHC03CP101 | DEMIN WATER PUMP-C SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313264 |  | 10295567 | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
6 | KIPP00 | 00GHC03CP102 | DEMIN WATER PUMP-C SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313092 |  | 10295582 | ZM06 |  |  | 10LAB01GH101
7 | KIPP00 | 00GHC04CP101 | EMERGENCY M/U PUMP-A SUCTION PT |  | -1 | 100 | -1 | 5 | Bar | YOKOGAWA | EJA530E | 91S313216 |  | 10295594 | ZM06 |  |  | 10LAB02GH101
8 | KIPP00 | 00GHC04CP102 | EMERGENCY M/U PUMP-A SUCTION STRAINER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313106 |  | 10295606 | ZM06 |  |  | 10LAB02GH101
9 | KIPP00 | 00GHC05CP101 | EMERGENCY M/U PUMP-B SUCTION PT |  | -1 | 100 | -1 | 5 | Bar | YOKOGAWA | EJA530E | 91S313214 |  | 10295616 | ZM06 |  |  | 10LAB06GH101
10 | KIPP00 | 00GHC05CP102 | EMERGENCY M/U PUMP-B SUCTION STRAINER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313105 |  | 10295627 | ZM06 |  |  | 10LAB06GH101
11 | KIPP00 | 00GHC10CP101 | DEMIN. WATER SUPPLY PUMP DISC. PRESS. A |  | -1 | 20 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313246 |  | 10295638 | ZM06 | OK |  | 10LAB06GH101
12 | KIPP00 | 00GHC10CP102 | DEMIN. WATER SUPPLY PUMP DISC. PRESS. B |  | -1 | 20 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313247 |  | 10295647 | ZM06 | OK |  | 10LAB10GH101
13 | KIPP00 | 00GHC16CP101 | EMERGENCY M/U DISCAHARGE PT - A |  | -1 | 100 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313302 |  | 10295648 | ZM06 | OK |  | 10LAB10GH101
14 | KIPP00 | 00GHC16CP102 | EMERGENCY M/U DISCAHARGE PT - B |  | -1 | 100 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313303 |  | 10295685 | ZM06 | OK |  | 10LAB01GH101
15 | KIPP00 | 00GHC24CF101 | CONDENSER MAKE UP WATER FIT |  | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313065 |  | 10295720 | ZM06 |  |  | 10LAB02GH101
16 | KIPP00 | 00GKB21CP101 | POTABLE WATER SUPPLY PUMP-A SUCTION PT |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313267 |  | 10295755 | ZM06 | OK |  | 10LAB02GH101
17 | KIPP00 | 00GKB22CP101 | POTABLE WATER SUPPLY PUMP-B SUCTION PT |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313268 |  | 10295760 | ZM06 | OK |  | 10LAB15GH101
18 | KIPP00 | 00GKB30CP101 | POTABLE WATER SUPPLY PUMP DISCHARGE PT - A |  | -1 | 20 | 0 | 9 | Bar | YOKOGAWA | EJA530E | 91S313244 |  | 10295769 | ZM06 | OK |  | 10LAB15GH101
19 | KIPP00 | 00GKB30CP102 | POTABLE WATER SUPPLY PUMP DISCHARGE PT - B |  | -1 | 20 | 0 | 9 | Bar | YOKOGAWA | EJA530E | 91S313245 |  | 10295777 | ZM06 | OK |  | 10LAB15GH101
20 | KIPP10 | 10LAA00CL101 | DEAERATOR & FW STORAGE TANK LEVEL A |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313099 |  | 10295785 | ZM06 | OK |  | 10LAB15GH101
21 | KIPP10 | 10LAA00CL102 | DEAERATOR & FW STORAGE TANK LEVEL B |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313098 |  | 10295819 | ZM06 | OK |  | 10LAB15GH101
22 | KIPP10 | 10LAA00CL103 | DEAERATOR & FW STORAGE TANK LEVEL C |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313095 |  | 10295759 | ZM06 | OK |  | 10LAB10GH101
23 | KIPP10 | 10LAA00CL104 | DEAERATOR & FW STORAGE TANK LEVEL D |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313094 |  | 10295820 | ZM06 | OK |  | 10LAB10GH101
24 | KIPP10 | 10LAA00CL105 | DEAERATOR & FW STORAGE TANK LEVEL E |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313093 |  | 10295831 | ZM06 | OK |  | 10LAB01GH101
25 | KIPP10 | 10LAA00CP101 | DEAERATOR & FW STORAGE TANK PRESSURE A |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313278 |  | 10295841 | ZM06 | OK |  | 10LAB02GH101
26 | KIPP10 | 10LAA00CP102 | DEAERATOR & FW STORAGE TANK PRESSURE B |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313279 |  | 10295851 | ZM06 | OK |  | 10LAB02GH101
27 | KIPP10 | 10LAA00CP103 | DEAERATOR & FW STORAGE TANK PRESSURE C |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313280 |  | 10296179 | ZM06 | OK
28 | KIPP10 | 10LAB01CP102 | STG 10 BOILER FWP C SUCTION PRESSURE |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213232 |  | 10296180 | ZM06 | OK
29 | KIPP10 | 10LAB02CP102 | BOILER FEED WATER PUMP B SUCTION PT |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213233 |  | 10296213 | ZM06 | OK
30 | KIPP10 | 10LAB03CP102 | STG 10 BOILER FWP C SUCTION PRESSURE |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213234 |  | 10296214 | ZM06 | OK
31 | KIPP10 | 10LAB06CP102 | CPH PUMP-A SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313235 |  | 10296232 | ZM06 | OK
32 | KIPP10 | 10LAB07CP102 | CPH PUMP-B SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313236 |  | 10296242 | ZM06 | OK
33 | KIPP10 | 10LAB08CP102 | CPH PUMP-C SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313237 |  | 10296283 | ZM06 | OK
34 | KIPP10 | 10LAB10CP101 | BOILER FEED WATER PUMP-A HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S313320 |  | 10296284 | ZM06 | OK
35 | KIPP10 | 10LAB10CP102 | BOILER FEED WATER PUMP-B HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S313321 |  | 10296285 | ZM06 | OK
36 | KIPP10 | 10LAB11CF101 | BOILER FEED WATER PUMP A HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313539 |  | 10296286 | ZM06 | OK
37 | KIPP10 | 10LAB11CF102 | BOILER FEED WATER PUMP A HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313542 |  | 10296356 | ZM06 | OK
38 | KIPP10 | 10LAB11CP101 | BOILER FEED WATER PUMP-A HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213317 |  | 10296357 | ZM06 | OK
39 | KIPP10 | 10LAB12CF101 | BOILER FEED WATER PUMP B HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313540 |  | 10296379 | ZM06 | OK
40 | KIPP10 | 10LAB12CF102 | BOILER FEED WATER PUMP B HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313543 |  | 10296393 | ZM06 | OK
41 | KIPP10 | 10LAB12CP101 | BOILER FEED WATER PUMP-B HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213318 |  | 10296407 | ZM06 | OK
42 | KIPP10 | 10LAB13CF101 | BOILER FEED WATER PUMP C HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313541 |  | 10296455 | ZM06 | OK
43 | KIPP10 | 10LAB13CF102 | BOILER FEED WATER PUMP C HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313544 |  | 10296456 | ZM06 | OK
44 | KIPP10 | 10LAB13CP101 | BOILER FEED WATER PUMP-C HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213319 |  | 10296457 | ZM06 | OK
45 | KIPP10 | 10LAB15CP101 | CPH PUMP DISCHARGE LINE PT A |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313311 |  | 10296467 | ZM06 | OK
46 | KIPP10 | 10LAB15CP102 | CPH PUMP DISCHARGE LINE PT B |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313312 |  | 10296476 | ZM06 | OK
47 | KIPP10 | 10LAB16CP101 | CPH PUMP-A DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S213304 |  | 10296485 | ZM06 | OK
48 | KIPP10 | 10LAB17CP101 | CPH PUMP-B DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313305 |  | 10298940 | ZM06 | OK
49 | KIPP10 | 10LAB18CP101 | CPH PUMP-C DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313306 |  | 10298941 | ZM06 | OK
50 | KIPP10 | 10LAB24CF101 | CRH STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 2500 | mmH2O | YOKOGAWA | EJA110E | 91S313064 |  | 10298942 | ZM06 | OK
51 | KIPP10 | 10LAB30CP101 | BOILER FEED WATER PUMP IP DISCHARGE PT-A |  | -1 | 500 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313218 |  | 10298998 | ZM06 | OK
52 | KIPP10 | 10LAB30CP102 | BOILER FEED WATER PUMP IP DISCHARGE PT-B |  | -1 | 500 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313220 |  | 10298999 | ZM06 | OK
53 | KIPP10 | 10LAB31CP101 | BFWP A IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313299 |  | 10299000 | ZM06 | OK
54 | KIPP10 | 10LAB32CP101 | BFWP B IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313300 |  | 10299082 | ZM06 | OK
55 | KIPP10 | 10LAB33CP101 | BFWP C IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313301 |  | 10299083 | ZM06 | OK
56 | KIPP10 | 10LBA10CP001 | P LP STEAM BFR ST | 2026-03-23 | -1 | 20 | -1 | 10 | Bar | YOKOGAWA | EJA530E | 91S313251 |  | 10299084 | ZM06 | OK
57 | KIPP10 | 10LBA10CP002 | P LP STEAM BFR ST | 2026-03-23 | -1 | 20 | -1 | 10 | Bar | YOKOGAWA | EJA530E | 91S313252 |  | 10299199 | ZM06 | OK
58 | KIPP10 | 10LBA50CP001 | P HP STEAM BFR ST | 2026-03-18 | -1 | 500 | -1 | 150 | Bar | YOKOGAWA | EJA530E | 91S313322 |  | 10299271 | ZM06 | OK
59 | KIPP10 | 10LBA50CP002 | P HP STEAM BFR ST | 2026-03-18 | -1 | 500 | -1 | 150 | Bar | YOKOGAWA | EJA530E | 91S313323 |  | 10299366 | ZM06 | OK
60 | KIPP10 | 10LBB41CP001 | P IP STEAM BFR ST | 2026-03-18 | -1 | 100 | -1 | 40 | Bar | YOKOGAWA | EJA530E | 91S313307 |  | 10299391 | ZM06 | OK
61 | KIPP10 | 10LBB42CP001 | P IP STEAM BFR ST | 2026-03-18 | -1 | 100 | -1 | 40 | Bar | YOKOGAWA | EJA530E | 91S313308 |  | 10299398 | ZM06 | OK
62 | KIPP10 | 10LBC10CP001 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313289 |  | 10299399 | ZM06 | OK
63 | KIPP10 | 10LBC10CP002 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313290 |  | 10299422 | ZM06 | OK
64 | KIPP10 | 10LBC10CP003 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313291 |  | 10299442 | ZM06 | OK
65 | KIPP10 | 10LBC10CP101 | STG 10 COLD REHEAT STEAM PRESS. | 2026-03-18 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313286 |  | 10299447 | ZM06 | OK
66 | KIPP10 | 10LBG00CP101 | AUXILIARY STEAM LINE PRESS. | 2026-03-23 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313292 |  | 10299448 | ZM06 | OK
67 | KIPP10 | 10LBG00CP102 | AUXILIARY STEAM LINE PRESS. | 2026-03-23 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313293 |  | 10299480 | ZM06 | OK
68 | KIPP10 | 10LCA01CP102 | CONDENSATE EXTRACTION PUMP-A SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313253 |  | 10299508 | ZM06
69 | KIPP10 | 10LCA02CP102 | CONDENSATE EXTRACTION PUMP-B SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313254 |  | 10299516 | ZM06
70 | KIPP10 | 10LCA03CP102 | CONDENSATE EXTRACTION PUMP-C SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313255 |  | 10299517 | ZM06
71 | KIPP10 | 10LCA10CF101 | CONDENSATE EXTRACTION PUMP DISCHARGE FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313066 |  | 10299531 | ZM06
72 | KIPP10 | 10LCA10CF102 | CONDENSATE EXTRACTION PUMP DISCHARGE FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313101 |  | 10299586 | ZM06
73 | KIPP10 | 10LCA10CP101 | CONDENSATE EXTRACTION PUMP DISCHARGE PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313297 |  | 10299593 | ZM06 | OK
74 | KIPP10 | 10LCA10CP102 | GLAND STEAM CONDENSER OUTLET PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313298 |  | 10299601 | ZM06 | OK
75 | KIPP10 | 10LCA10CP103 | CONDENSATE EXTRACTION PUMP DISCHARGE PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313310 |  | 10299602 | ZM06 | OK
76 | KIPP10 | 10LCA11CP101 | CEP-A DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313294 |  | 10301365 | ZM06
77 | KIPP10 | 10LCA12CP101 | CEP-B DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313295 |  | 10301366 | ZM06
78 | KIPP10 | 10LCA13CP101 | CEP-C DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313296 |  | 10301367 | ZM06
79 | KIPP10 | 10LCA20CF101 | DEAERATOR & FW STORAGE TANK INLET FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313069 |  | 10301423 | ZM06 | OK
80 | KIPP10 | 10MAA10CP001 | P UPSTR HPT BLADING |  | -1.013 | 275.789 | -1 | 150 | Bar | ROSEMOUNT | 3051 PT | 9834864 |  | 10301424 | ZM06 | OK
81 | KIPP10 | 10MAA10CT031A | HP TURBINE EXHAUST THERMOCOUPLE |  | - | - | - | - | ᵒC | - | - | - |  | 10301425 | ZM06 | OK
82 | KIPP10 | 10MAA10CT031B | HP TURBINE EXHAUST THERMOCOUPLE |  | - | - | - | - | ᵒC | - | - | - |  | 10301507 | ZM06 | OK
83 | KIPP10 | 10MAB10CP001 | P UPSTR IPT BLADING |  | -137.89 | 137.89 | -1 | 40 | Bar | ROSEMOUNT | 3051 PT | 9834862 |  | 10301508 | ZM06 | OK
84 | KIPP10 | 10MAB10CP002 | P UPSTR IPT BLADING |  | -137.89 | 137.89 | -1 | 40 | Bar | ROSEMOUNT | 3051 PT | 9834863 |  | 10301509 | ZM06 | OK
85 | KIPP10 | 10MAC01CP021 | LP TUR.UPER STR.CROSS PIPE PRESSURE |  | -20.684 | 20.684 | -1 | 8 | Bar | ROSEMOUNT | 3051 PT | 9834860 |  | 10301647 | ZM06 | OK
86 | KIPP10 | 10MAC01CP022 | LP TUR.UPER STR.CROSS PIPE PRESSURE |  | -20.684 | 20.684 | -1 | 8 | Bar | ROSEMOUNT | 3051 PT | 9834861 |  | 10301724 | ZM06 | OK
87 | KIPP10 | 10MAC10CP031 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861934 |  | 10306306 | ZM06 | OK
88 | KIPP10 | 10MAC10CP032 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861935 |  | 10301849 | ZM06 | OK
89 | KIPP10 | 10MAC10CP033 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861936 |  | 10301856 | ZM06 | OK
90 | KIPP10 | 10MAV40CP003 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843509 |  | 10301857 | ZM06 | OK
91 | KIPP10 | 10MAV40CP004 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843508 |  | 10301880 | ZM06 | OK
92 | KIPP10 | 10MAV40CP005 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843510 |  | 10301911 | ZM06 | OK
93 | KIPP10 | 10MAW02CP001 | GLAND STEAM LINE PT |  | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313309 |  | 10301917 | ZM06 | OK
94 | KIPP10 | 10MAW10CT001 | GLAND STEAM SEALING SYSTEM |  | - | - | - | - | ᵒC | - | - | - |  | 10301918 | ZM06 | OK
95 | KIPP10 | 10MAW10CT002 | GLAND STEAM SEALING SYSTEM |  | - | - | - | - | ᵒC | - | - | - |  | 10301950 | ZM06 | OK
96 | KIPP10 | 10MAW15CP001 | GLAND STEAM SEALING SYSTEM PRESSURE |  | -2486.4 | 2486.4 | -150 | 350 | mBar | ROSEMOUNT | 3051 PT | 9834859 |  | 10301985 | ZM06 | OK
97 | KIPP10 | 10MAX11CP031 | P HYDR HEADER |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843512 |  | 10301995 | ZM06 | OK
98 | KIPP10 | 10MAX44CP001 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843513 |  | 10301996 | ZM06 | OK
99 | KIPP10 | 10MAX44CP002 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843511 |  | 10302010 | ZM06 | OK
100 | KIPP10 | 10MAX44CP003 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843514 |  | 10302085 | ZM06 | OK
101 | KIPP10 | 10MKA13CP111 | GEN.AIR BLOWER FILTER PRESSURE |  | -1013.2 | 2068.4 | -50 | 0 | mBar | ROSEMOUNT | 2088 PT | 9917083 |  | 10302093 | ZM06 | OK
102 | KIPP10 | 10MKA13CP112 | GEN.AIR BLOWER AFTER FAN PRESSURE |  | -1013.2 | 2068.4 | 0 | 400 | mBar | ROSEMOUNT | 2088 PT | 9917081 |  | 10302101 | ZM06 | OK
103 | KIPP10 | 10MKA13CP113 | GEN.AIR BLOWER AFTER FAN PRESSURE |  | -1013.2 | 2068.4 | 0 | 400 | mBar | ROSEMOUNT | 2088 PT | 9917082 |  | 10302102 | ZM06 | OK
104 | KIPP11 | 11EKG40CP101 | FG PERFORMANCE HEATER SKID OUTLET PRESS |  | -1 | 100 | 0 | 61 | Bar | YOKOGAWA | EJA530E | 91S313313 |  | 10291890 | ZM06 | OK
105 | KIPP11 | 11HAC22CF002 | LP FW FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214472 |  | 10295683 | ZM06 | OK
106 | KIPP11 | 11HAC22CF003 | LP FW FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214473 |  | 10295684 | ZM06 | OK
107 | KIPP11 | 11HAC25CP001 | IP ECO O/L PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051TG | 210426 |  | 10295718 | ZM06 | OK
108 | KIPP11 | 11HAC58CP001 | HP ECO O/L PT |  | 0 | 689.7 | 0 | 300 | Bar | ROSEMOUNT | 2050TG | 210420 |  | 10295719 | ZM06 | OK
109 | KIPP11 | 11HAD10CL001 | LP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576009 |  | 10295753 | ZM06
110 | KIPP11 | 11HAD10CL002 | LP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576010 |  | 10295754 | ZM06
111 | KIPP11 | 11HAD10CL003 | LP DRUM LT 3 | 3.04.2026 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576011 |  | 10295804 | ZM06
112 | KIPP11 | 11HAD10CP001 | LP DRUM PT 1 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576027 |  | 10296453 | ZM06 | OK
113 | KIPP11 | 11HAD10CP002 | LP DRUM PT 2 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576028 |  | 10296453 | ZM06 | OK
114 | KIPP11 | 11HAD10CP003 | LP DRUM PT 3 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576029 |  | 10296525 | ZM06 | OK
115 | KIPP11 | 11HAD30CL001 | IP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576006 |  | 10298762 | ZM06
116 | KIPP11 | 11HAD30CL002 | IP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576007 |  | 10298763 | ZM06
117 | KIPP11 | 11HAD30CL003 | IP DRUM LT 3 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576008 |  | 10299168 | ZM06
118 | KIPP11 | 11HAD30CP001 | IP DRUM PT 1 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575997 |  | 10299182 | ZM06 | OK |  | 10LAB10GH101
119 | KIPP11 | 11HAD30CP002 | IP DRUM PT 2 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575998 |  | 10296596 | ZM06 | OK
120 | KIPP11 | 11HAD30CP003 | IP DRUM PT 3 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575999 |  | 10296597 | ZM06 | OK
121 | KIPP11 | 11HAD50CL001 | HP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -39 | -1304 | mmH2O | ROSEMOUNT | 2051 PT | 3576004 |  | 10297154 | ZM06
122 | KIPP11 | 11HAD50CL002 | HP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -39 | -1301 | mmH2O | ROSEMOUNT | 2051 PT | 3576003 |  | 10297155 | ZM06 |  |  | Indikatör
123 | KIPP11 | 11HAD50CL003 | HP DRUM LT 3 |  | -6350 | 6350 | -39 | -1304 | mmH2O | ROSEMOUNT | 2051 PT | 3576005 |  | 10296592 | ZM06
124 | KIPP11 | 11HAD50CP001 | HP DRUM PT 1 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575991 |  | 10296623 | ZM06 | OK
125 | KIPP11 | 11HAD50CP002 | HP DRUM PT 2 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575992 |  | 10296624 | ZM06 | OK
126 | KIPP11 | 11HAD50CP003 | HP DRUM PT 3 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575993 |  | 10296662 | ZM06 | OK
127 | KIPP11 | 11LAB20CF101 | HP STEAM BYPASS SPRAYAY WATER FT |  | -6350 | 6350 | 0 | 6300 | mmH2O | ROSEMOUNT | 2051 PT | 214447 |  | 10296663 | ZM06 | OK
128 | KIPP11 | 11LAB31CF101 | FEED WATER FROM CONDENSATE PREHEATER FT |  | -10197.2 | 10197.2 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313068 |  | 10296671 | ZM06 | OK
129 | KIPP11 | 11LAB46CP001 | IP/LP FW PT | 2026-04-02 | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051 PT | 210430 |  | 10296672 | ZM06 | OK
130 | KIPP11 | 11LAB90CP001 | FEED WATER TO GT OTC STRAINER PDT |  | -5 | 5 | 0 | 2 | Bar | YOKOGAWA | EJA110E | 91S313545 |  | 10296673 | ZM06
131 | KIPP11 | 11LAB91CF101 | FW LP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816770 |  | 10297054 | ZM06
132 | KIPP11 | 11LAB91CF102 | FW LP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816771 |  | 10297055 | ZM06
133 | KIPP11 | 11LAB92CF101 | FW HP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816772 |  | 10297056 | ZM06
134 | KIPP11 | 11LAB92CF102 | FW HP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816773 |  | 10297144 | ZM06
135 | KIPP11 | 11LAB96CP001 | HP FW PT | 2026-04-02 | 0 | 289.3 | 0 | 300 | Bar | ROSEMOUNT | 2051 PT | 210424 |  | 10297163 | ZM06 | OK
136 | KIPP11 | 11LAE50CF002 | HP DESUPERHEATER SPRAY FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214454 |  | 10297207 | ZM06 | OK
137 | KIPP11 | 11LAE50CF003 | HP DESUPERHEATER SPRAY FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214455 |  | 10297266 | ZM06 | OK
138 | KIPP11 | 11LAF40CF002 | RH DESUPERHEATER SPRAY FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 322 | mBar | YOKOGAWA | EJA110E | 91S313058 |  | 10297267 | ZM06 | OK
139 | KIPP11 | 11LAF40CF003 | RH DESUPERHEATER SPRAY FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214469 |  | 10297268 | ZM06 | OK
140 | KIPP11 | 11LBA00CP101 | HP STEAM PRESSURE | 2026-03-17 | -1 | 500 | 0 | 151 | Bar | YOKOGAWA | EJA530E | 91S313315 |  | 10300500 | ZM06 | OK |  |  | Set:2,2 - Reset: 1,99
141 | KIPP11 | 11LBA10CF002 | LP STEAM O/L FT 1 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214474 |  | 10297306 | ZM06 | OK
142 | KIPP11 | 11LBA10CF003 | LP STEAM O/L FT 2 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214475 |  | 10297307 | ZM06 | OK
143 | KIPP11 | 11LBA10CP001 | LP STEAM PRESSURE | 2026-03-24 | -1 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 210437 |  | 10297308 | ZM06 | OK
144 | KIPP11 | 11LBA20CP101 | HP BYPASS VALVE OUTLET PRESSURE A | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313282 |  | 10298707 | ZM06 | OK
145 | KIPP11 | 11LBA20CP102 | HP BYPASS VALVE OUTLET PRESSURE B | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313283 |  | 10299767 | ZM06 | OK
146 | KIPP11 | 11LBA30CF002 | IP STEAM O/L FT 1 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214470 |  | 10299768 | ZM06 | OK
147 | KIPP11 | 11LBA30CF003 | IP STEAM O/L FT 2 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214471 |  | 10299769 | ZM06 | OK
148 | KIPP11 | 11LBA30CP001 | IP STEAM O/L PT |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210431 |  |  |  | OK
149 | KIPP11 | 11LBA31CP101 | LP STEAM PT | 2026-03-24 | -1 | 20 | 0 | 10 | Bar | YOKOGAWA | EJA530E | 91S313226 |  |  |  | OK
150 | KIPP11 | 11LBA40CP101 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313227 |  |  |  | OK
151 | KIPP11 | 11LBA40CP102 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313228 |  |  |  | OK
152 | KIPP11 | 11LBA50CF002 | HP STEAM O/L FT 1 | 2026-04-02 | -2486 | 2486 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214456 |  |  |  | OK
153 | KIPP11 | 11LBA50CF003 | HP STEAM O/L FT 2 | 2026-04-02 | -2486 | 2486 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214457 |  |  |  | OK
154 | KIPP11 | 11LBA50CP001 | HP STEAM PT | 2026-04-02 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 210425 |  |  |  | OK
155 | KIPP11 | 11LBB00CP101 | HOT REHEAT STEAM PT | 2026-03-17 | -1 | 100 | 0 | 50 | Bar | YOKOGAWA | EJA530E | 91S313213 |  |  |  | OK
156 | KIPP11 | 11LBB20CP101 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313222 |  |  |  | OK
157 | KIPP11 | 11LBB20CP102 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313223 |  | 10299968 | ZM06 | OK
158 | KIPP11 | 11LBB40CP001 | HOT REHEAT STEAM PT | 2026-04-02 | -1.01 | 275.79 | 0 | 50 | Bar | ROSEMOUNT | 2051 PT | 210432 |  | 10299969 | ZM06 | OK
159 | KIPP11 | 11LBC00CF101 | COLD REHEAT STEAM FLOW A | 2026-04-02 | -10197.2 | 10197.2 | 0 | 4756.2 | mmH2O | YOKOGAWA | EJA110E | 91S313071 |  | 10299972 | ZM06 | OK
160 | KIPP11 | 11LBC00CF102 | COLD REHEAT STEAM FLOW B | 2026-04-02 | -10197.2 | 10197.2 | 0 | 4756.2 | mmH2O | YOKOGAWA | EJA110E | 91S313072 |  | 10299973 | ZM06 | OK
161 | KIPP11 | 11LBC00CP101 | COLD REHEAT STEAM PRESSURE | 2026-04-02 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313287 |  | 10299974 | ZM06 | ok
162 | KIPP11 | 11LBC30CP001 | COLD REHEAT STEAM PT |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210433 |  | 10299975 | ZM06 | OK
163 | KIPP11 | 11LBG91CP001 | GT OTC OUT STEAM LINE PT-1 | 2026-04-02 | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S313324 |  | 10299976 | ZM06 | ok
164 | KIPP11 | 11LBG91CP002 | GT OTC OUT STEAM LINE PT-2 | 2026-04-02 | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S313326 |  | 10300011 | ZM06 | ok
165 | KIPP11 | 11LCA20CF101 | LP STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313062 |  | 10300012 | ZM06 | OK
166 | KIPP11 | 11LCA21CF101 | HOT REHEAT STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313060 |  | 10300015 | ZM06 | OK
167 | KIPP11 | 11MBA30CP001 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824805 |  | 10300054 | ZM06 | OK
168 | KIPP11 | 11MBA30CP003 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824806 |  | 10300054 | ZM06 | OK
169 | KIPP11 | 11MBA30CP004 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824807 |  | 10300096 | ZM06 | OK
170 | KIPP11 | 11MBA80CP051 | GT AFT COMPRESSOR 1H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825256 |  | 10300096 | ZM06 | OK
171 | KIPP11 | 11MBA80CP052 | GT AFT COMPRESSOR 4H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825257 |  | 10300101 | ZM06 | OK
172 | KIPP11 | 11MBA80CP054 | P AFT COMPRESSOR 8H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CD | 9825258 |  | 10300102 | ZM06 | OK
173 | KIPP11 | 11MBE41CP013 | GT H/F WATER PUMP SUCTION FILTER PDT |  |  |  | -1000 | 2200 | mBar | ROSEMOUNT | 2088TG | 2753518 |  | 10300106 | ZM06 | OK
174 | KIPP11 | 11MBE41CP121 | GT H/F WATER PUMP-1 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210595 |  | 10300107 | ZM06 | OK
175 | KIPP11 | 11MBE41CP122 | GT H/F WATER PUMP-2 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210445 |  | 10300113 | ZM06 | OK
176 | KIPP11 | 11MBE41CP123 | GT H/F WATER PUMP-3 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210429 |  | 10300114 | ZM06 | OK
177 | KIPP11 | 11MBE41CP124 | GT H/F WATER PUMP-4 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210446 |  | 10300131 | ZM06 | OK
178 | KIPP11 | 11MBE41CP141 | GT H/F WATER PUMP-1 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631493 |  | 10300132 | ZM06 | OK
179 | KIPP11 | 11MBE41CP142 | GT H/F WATER PUMP-2 DISCHARGE PT |  | -14.7 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 607375 |  | 10300133 | ZM06 | OK
180 | KIPP11 | 11MBE41CP143 | GT H/F WATER PUMP-3 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631492 |  |  |  | OK
181 | KIPP11 | 11MBE41CP144 | GT H/F WATER PUMP-4 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631494 |  | 10300278 | ZM06 | OK
182 | KIPP11 | 11MBH20CP007 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825262 |  | 10300298 | ZM06 | OK
183 | KIPP11 | 11MBH20CP008 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825263 |  | 10300345 | ZM06 | OK
184 | KIPP11 | 11MBH20CP009 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825264 |  | 10300346 | ZM06 | OK
185 | KIPP11 | 11MBH30CL001 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-19 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313549 |  | 10300347 | ZM06 | OK
186 | KIPP11 | 11MBH30CL002 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-19 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313550 |  | 10300363 | ZM06 | OK
187 | KIPP11 | 11MBH30CP003 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 PT | 9825259 |  | 10300364 | ZM06 | OK
188 | KIPP11 | 11MBH30CP004 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 PT | 9825260 |  | 10300365 | ZM06 | OK
189 | KIPP11 | 11MBH30CP005 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825261 |  | 10300374 | ZM06 | OK
190 | KIPP11 | 11MBH30CP015 | PRESSURE DIFF ACROSS LP AIR COOLER | 2026-01-19 | -20.684 | 20.684 | 0 | 4 | Bar | ROSEMOUNT | 3051 PT | 9824811 |  | 10300375 | ZM06 | OK
191 | KIPP11 | 11MBH30CP020 | P QUENSCH WATER TO LP COOLER | 2026-01-20 | -137.89 | 137.89 | 0 | 30 | Bar | ROSEMOUNT | 3051 PT | 9825287 |  | 10300376 | ZM06 | OK
192 | KIPP11 | 11MBH30CP021 | GT SEV COMBUSTOR LINER/KA01 PDT | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825276 |  | 10300420 | ZM06 | OK
193 | KIPP11 | 11MBH30CP022 | P DIFF SEV COMBUSTOR LINER/KA01 | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825274 |  | 10300469 | ZM06 | OK
194 | KIPP11 | 11MBH30CP023 | P DIFF SEV COMBUSTOR LINER/KA01 | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825275 |  | 10300469 | ZM06 | OK
195 | KIPP11 | 11MBH40CL001 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-20 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313547 |  | 10300469 | ZM06 | OK
196 | KIPP11 | 11MBH40CL002 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-20 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313548 |  | 10300478 | ZM06 | OK
197 | KIPP11 | 11MBH40CP015 | DP HP OTC | 2026-01-20 | -621.6 | 621.6 | 0 | 500 | mBar | ROSEMOUNT | 3051 PT | 9825290 |  | 10300497 | ZM06 | OK
198 | KIPP11 | 11MBH41CP102 | PRESSURE AFTER BLOW-OFF BYPASS VALVE | 2026-01-20 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CD | 9855800 |  | 10300498 | ZM06 | OK
199 | KIPP11 | 11MBH41CP103 | DP FLOW MEASUREMENT | 2026-01-20 | -20.684 | 20.684 | 0 | 10 | Bar | ROSEMOUNT | 3051CD | 9855803 |  | 10300499 | ZM06 | OK
200 | KIPP11 | 11MBH52CP001 | EXHAUST BEARING FAN 1 PDI | 2026-01-20 | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891371 |  | 10300563 | ZM06 | OK
201 | KIPP11 | 11MBH52CP002 | EXHAUST BEARING FAN 2 PDI | 2026-01-20 | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891372 |  | 10300564 | ZM06 | OK
202 | KIPP11 | 11MBH60CP001 | DP CMAS FAN 1 | 2026-01-20 | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891369 |  |  |  | OK
203 | KIPP11 | 11MBH60CP002 | DP CMAS FAN 2 | 2026-01-20 | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891370 |  | 10300662 | ZM06 | OK
204 | KIPP11 | 11MBH80CP011 | DIFFERENTIAL PRESSURE EV COMBUSTOR | 2026-01-20 | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825280 |  | 10303004 | ZM06 | OK
205 | KIPP11 | 11MBH80CP012 | DIFFERENTIAL PRESSURE EV COMBUSTOR | 2026-01-20 | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825281 |  | 10301132 | ZM06 | OK
206 | KIPP11 | 11MBH90CP001 | PRESSURE BEFORE ANTI-ICING CONTROL VALVE | 2026-01-21 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914214 |  | 10302272 | ZM06 | OK
207 | KIPP11 | 11MBH90CP004 | DP OVER ANTI ICING CV | 2026-01-21 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914216 |  | 10302273 | ZM06 | OK
208 | KIPP11 | 11MBL01CP011 | DP AIR INTK FLTR TOT | 2026-01-21 | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 9844811 |  | 10302274 | ZM06 | OK
209 | KIPP11 | 11MBL01CP012 | DP AIR INTK FLTR TOT | 2026-01-21 | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 9844812 |  | 10302473 | ZM06 | OK
210 | KIPP11 | 11MBL51CP001 | DP PRE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844805 |  | 10302474 | ZM06 | OK
211 | KIPP11 | 11MBL51CP002 | DP FINE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844806 |  | 10302477 | ZM06 | OK
212 | KIPP11 | 11MBL51CP012 | DP FINE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844807 |  | 10302478 | ZM06 | OK
213 | KIPP11 | 11MBL61CP010 | EVAP COOLER PUMP AFTER PRESSURE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051CD | 9852954 |  | 10302479 | ZM06 | OK
214 | KIPP11 | 11MBP01CP003 | FUEL GAS FILTER DP | 2026-01-21 | -2.4864 | 2.4864 | 0 | 1.5 | Bar | ROSEMOUNT | 3051 PT | 9789262 |  | 10302480 | ZM06 | OK
215 | KIPP11 | 11MBP05CP102 | EV FUEL GAS FLOW PT | 2026-01-21 | 0 | 55.16 | 0 | 55 | Bar | ROSEMOUNT | 3051 PT | 9846441 |  | 10302481 | ZM06 | OK
216 | KIPP11 | 11MBP41CP001 | P AFT TRIP SOV EV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782024 |  | 10302516 | ZM06 | OK
217 | KIPP11 | 11MBP41CP004 | DP CV EV STG2 | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782030 |  | 10302517 | ZM06 | OK
218 | KIPP11 | 11MBP41CP006 | P AFT CV FGAS EV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782025 |  | 10302520 | ZM06 | OK
219 | KIPP11 | 11MBP42CP001 | P BEF FGAS TRIP SOV SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782026 |  | 10302559 | ZM06 | OK
220 | KIPP11 | 11MBP42CP004 | DP CV FGAS SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782031 |  | 10302601 | ZM06 | OK
221 | KIPP11 | 11MBP42CP006 | P AFT CV FGAS SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782027 |  | 10302606 | ZM06 | OK
222 | KIPP11 | 11MBP43CP001 | P BFR CV EV STG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782028 |  | 10302607 | ZM06 | OK
223 | KIPP11 | 11MBP43CP004 | DP CV EVSTG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782032 |  | 10302611 | ZM06 | OK
224 | KIPP11 | 11MBP43CP006 | P AFT CV EV STG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782029 |  | 10302612 | ZM06 | OK
225 | KIPP11 | 11MBV10CP001 | PRESSURE LUBE OIL TANK | 2026-01-22 | -621.6 | 621.6 | 0 | 60 | mBar | ROSEMOUNT | 3051 PT | 9781969 |  | 10302618 | ZM06 | OK
226 | KIPP11 | 11MBV21CP001 | P AFT LUBE OIL PMP 1 | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791817 |  | 10302619 | ZM06 | OK
227 | KIPP11 | 11MBV21CP002 | P AFT LUBE OIL PMP 2 | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791818 |  | 10302636 | ZM06 | OK
228 | KIPP11 | 11MBV21CP003 | LUBE OIL FILTER DP | 2026-01-22 | -2.4864 | 2.4864 | -2.5 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9781970 |  | 10302637 | ZM06 | OK
229 | KIPP11 | 11MBV22CP001 | EMERGENCY LUBE OIL PUMP AFTER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791819 |  | 10302638 | ZM06 | OK
230 | KIPP11 | 11MBV40CP001 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791820 |  | 10302783 | ZM06 | OK
231 | KIPP11 | 11MBV40CP002 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791821 |  | 10302803 | ZM06 | OK
232 | KIPP11 | 11MBV40CP003 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791822 |  | 10302850 | ZM06 | OK
233 | KIPP11 | 11MBV40CP006 | P LUBE OIL HEADER 6 ( PRESSURE SWITCH ) | 2026-01-22 | 0 | 10 | - | 2.11 | Bar | Trafog | Switch | - |  | 10302851 | ZM06 | OK
234 | KIPP11 | 11MBX21CP001 | P AFT PWR OIL PMP 2 | 2026-01-22 | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791823 |  | 10302852 | ZM06 | OK
235 | KIPP11 | 11MBX21CP002 | P AFT PWR OIL PMP 1 | 2026-01-22 | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791824 |  | 10302868 | ZM06 | OK
236 | KIPP11 | 11MBX21CP010 | GT P/O TWIN FILTER PDT | 2026-01-22 | -20.684 | 20.684 | -2 | 8 | Bar | ROSEMOUNT | 3051CD | 9782033 |  | 10302869 | ZM06 | OK
237 | KIPP11 | 11MBX42CP001 | P HYDR SAFETY SYS | 2026-01-22 | -137.89 | 137.89 | 0 | 60 | Bar | ROSEMOUNT | 3051 PT | 9782034 |  | 10302870 | ZM06 | OK
238 | KIPP12 | 12EKG40CP101 | FG PERFORMANCE HEATER SKID OUTLET PRESS |  | -1 | 100 | 0 | 61 | Bar | YOKOGAWA | EJA530E | 91S313314 |  | 10302879 | ZM06
239 | KIPP12 | 12HAC22CF002 | LP FW FT 1 |  | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 3576023 |  | 10302880 | ZM06 | OK
240 | KIPP12 | 12HAC22CF003 | LP FW FT 2 |  | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214485 |  | 10302881 | ZM06 | OK
241 | KIPP12 | 12HAC25CF002 | IP DRUM FW FLOW A |  | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214478 |  | 10302924 | ZM06 | OK
242 | KIPP12 | 12HAC25CF003 | IP DRUM FW FLOW B |  | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214479 |  | 10302973 | ZM06 | OK
243 | KIPP12 | 12HAC25CP001 | IP ECO O/L PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051TG | 210444 |  | 10302982 | ZM06
244 | KIPP12 | 1: 12HAC58CF002; 2: HP ECO O/L FT 1; 9: ROSEMOUNT |  |  |  | OK
245 | KIPP12 | 1: 12HAC58CF003; 2: HP ECO O/L FT 2; 9: ROSEMOUNT |  |  |  | OK
246 | KIPP12 | 12HAC58CP001 | HP ECO O/L PT |  | 0 | 689.7 | 0 | 300 | Bar | ROSEMOUNT | 2050TG | 210438 |  | 10303001 | ZM06 | OK
247 | KIPP12 | 12HAD10CL001 | LP DRUM LT 1 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576021 |  | 10303002 | ZM06 | OK
248 | KIPP12 | 12HAD10CL002 | LP DRUM LT 2 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576022 |  | 10303003 | ZM06 | OK
249 | KIPP12 | 12HAD10CL003 | LP DRUM LT 3 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576023 |  | 10303067 | ZM06 | OK
250 | KIPP12 | 12HAD10CP001 | LP DRUM PT 1 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576030 |  | 10303068 | ZM06 | OK
251 | KIPP12 | 12HAD10CP002 | LP DRUM PT 2 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576031 |  | 10303166 | ZM06 | OK
252 | KIPP12 | 12HAD10CP003 | LP DRUM PT 3 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576032 |  | 10301187 | ZM06 | OK
253 | KIPP12 | 12HAD30CL001 | IP DRUM LT 1 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576018 |  | 10301188 | ZM06 | OK
254 | KIPP12 | 12HAD30CL002 | IP DRUM LT 2 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576019 |  | 10301613 | ZM06 | OK
255 | KIPP12 | 12HAD30CL003 | IP DRUM LT 3 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576020 |  | 10301630 | ZM06 | OK |  | 10LAB10GH101
256 | KIPP12 | 12HAD30CP001 | IP DRUM PT 1 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576000 |  | 10301758 | ZM06 | OK
257 | KIPP12 | 12HAD30CP002 | IP DRUM PT 2 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576001 |  | 10301759 | ZM06 | OK
258 | KIPP12 | 12HAD30CP003 | IP DRUM PT 3 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576002 |  | 10301801 | ZM06 | OK
259 | KIPP12 | 12HAD50CL001 | HP DRUM LT 1 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576015 |  | 10301802 | ZM06 | OK
260 | KIPP12 | 12HAD50CL002 | HP DRUM LT 2 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576016 |  | 10301847 | ZM06 | OK
261 | KIPP12 | 12HAD50CL003 | HP DRUM LT 3 |  | -6350 | 6350 | -33 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576017 |  | 10301848 | ZM06 | OK
262 | KIPP12 | 12HAD50CP001 | HP DRUM PT 1 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575994 |  | 10301878 | ZM06 | OK
263 | KIPP12 | 12HAD50CP002 | HP DRUM PT 2 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575995 |  | 10301879 | ZM06 | OK
264 | KIPP12 | 12HAD50CP003 | HP DRUM PT 3 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575996 |  | 10301187 | ZM06 | OK
265 | KIPP12 | 12LAB20CF101 | HP STEAM BYPASS SPRAYAY WATER FT |  | -6350 | 6350 | 0 | 6300 | mmH2O | ROSEMOUNT | 2051 PT | 214441 |  | 10301879 | ZM06 | OK
266 | KIPP12 | 12LAB31CF101 | FW FROM CONDENSATE PREHEATER FT |  | -10197.2 | 10197.2 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313067 |  | 10301188 | ZM06 | OK
267 | KIPP12 | 12LAB46CP001 | IP/LP FW PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051 PT | 210448 |  | 10301358 | ZM06 | OK
268 | KIPP12 | 12LAB96CP001 | HP FW PT |  | 0 | 689.5 | 0 | 300 | Bar | ROSEMOUNT | 2051 PT | 210442 |  | 10301359 | ZM06 | OK
269 | KIPP12 | 12LAE50CF002 | HP DESUPERHEATER SPRAY FT 1 |  | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214465 |  | 10301360 | ZM06 | OK
270 | KIPP12 | 12LAE50CF003 | HP DESUPERHEATER SPRAY FT 2 |  | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214466 |  | 10301365 | ZM06 | OK
271 | KIPP12 | 12LAF40CF002 | RH DESUPERHEATER SPRAY FT 1 |  | -635 | 635 | 0 | 322 | mbar | YOKOGAWA | EJA110E | 91S313100 |  | 10301366 | ZM06 | OK
272 | KIPP12 | 12LAF40CF003 | RH DESUPERHEATER SPRAY FT 2 |  | -635 | 635 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214481 |  | 10301367 | ZM06 | OK
273 | KIPP12 | 12LBA00CP101 | HIGH PRESSURE STEAM PRESSURE | 2026-03-17 | -1 | 500 | 0 | 151 | Bar | ROSEMOUNT | EJA530E | 91S313316 |  | 10301416 | ZM06 | OK
274 | KIPP12 | 12LBA10CF002 | LP STEAM O/L FT 1 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214635 |  | 10301802 | ZM06 | OK
275 | KIPP12 | 12LBA10CF003 | LP STEAM O/L FT 2 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214636 |  | 10306306 | ZM06 | OK
276 | KIPP12 | 12LBA10CP001 | LP STEAM PT | 2026-03-24 | -1 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 210454 |  | 10301847 | ZM06 | OK
277 | KIPP12 | 12LBA20CP101 | HP BYPASS VALVE OUTLET PRESSURE A | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313284 |  | 10301848 | ZM06 | OK
278 | KIPP12 | 12LBA20CP102 | HP BYPASS VALVE OUTLET PRESSURE B | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313285 |  | 10301849 | ZM06 | OK
279 | KIPP12 | 12LBA30CF002 | IP STEAM O/L FT 1 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214482 |  | 10301417 | ZM06 | OK
280 | KIPP12 | 12LBA30CF003 | IP STEAM O/L FT 2 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214483 |  | 10301418 | ZM06 | OK
281 | KIPP12 | 12LBA30CP001 | IP STEAM O/L PT |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210449 |  | 10301423 | ZM06 | OK
282 | KIPP12 | 12LBA31CP101 | LP STEAM PT | 2026-03-24 | -1 | 20 | 0 | 10 | Bar | YOKOGAWA | EJA530E | 91S313229 |  | 10301424 | ZM06 | OK
283 | KIPP12 | 12LBA40CP101 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313230 |  | 10301425 | ZM06 | OK
284 | KIPP12 | 12LBA40CP102 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313231 |  | 10295559 | ZM06 | OK
285 | KIPP12 | 12LBA50CF002 | HP STEAM O/L FT 1 |  | -2468 | 2468 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214476 |  | 10295560 | ZM06 | OK
286 | KIPP12 | 12LBA50CF003 | HP STEAM O/L FT 2 |  | -2468 | 2468 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214477 |  | 10295561 | ZM06 | OK
287 | KIPP12 | 12LBA50CP001 | HP STEAM PT |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 210443 |  | 10295562 | ZM06 | OK
288 | KIPP12 | 12LBB00CP101 | HOT REHEAT STEAM PT | 2026-03-17 | -1 | 500 | 0 | 50 | Bar | YOKOGAWA | EJA530E | 91S313215 |  | 10295563 | ZM06 | OK
289 | KIPP12 | 12LBB20CP101 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313224 |  | 10301911 | ZM06 | OK
290 | KIPP12 | 12LBB20CP102 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313225 |  | 10301917 | ZM06 | OK
291 | KIPP12 | 12LBB40CP001 | RH STEAM PT |  | -1.01 | 275.79 | 0 | 50 | Bar | ROSEMOUNT | 2051 PT | 210450 |  | 10301918 | ZM06 | OK
292 | KIPP12 | 12LBC00CF101 | COLD REHEAT STEAM FLOW A |  | -10197.2 | 10197.2 | 0 | 2312 | mmH2O | YOKOGAWA | EJA110E | 91S313073 |  | 10301948 | ZM06 | OK
293 | KIPP12 | 12LBC00CF102 | COLD REHEAT STEAM FLOW B |  | -10197.2 | 10197.2 | 0 | 2312 | mmH2O | YOKOGAWA | EJA110E | 91S313074 |  | 10301949 | ZM06 | OK
294 | KIPP12 | 12LBC00CP101 | COLD REHEAT STEAM PRESSURE |  | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S213288 |  | 10301950 | ZM06 | OK
295 | KIPP12 | 12LBC30CP001 | COLD REHEAT PRESSURE |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210451 |  | 10301985 | ZM06 | OK
296 | KIPP12 | 12LBG91CP001 | GT OTC OUT STEAM LINE PT-1 |  | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S213325 |  | 10301995 | ZM06 | OK
297 | KIPP12 | 12LBG91CP002 | GT OTC OUT STEAM LINE PT-1 |  | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S213327 |  | 10301996 | ZM06 | OK
298 | KIPP12 | 12LCA20CF101 | LP STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313063 |  | 10302010 | ZM06 | OK
299 | KIPP12 | 12LCA21CF101 | HOT REHEAT STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313061 |  | 10302077 | ZM06 | OK
300 | KIPP12 | 12MBA30CP001 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824808 |  | 10302078 | ZM06
301 | KIPP12 | 12MBA30CP003 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824809 |  | 10302085 | ZM06
302 | KIPP12 | 12MBA30CP004 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824810 |  | 10302093 | ZM06
303 | KIPP12 | 12MBA80CP051 | GT AFT COMPRESSOR 1H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825265 |  | 10302101 | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
304 | KIPP12 | 12MBA80CP052 | GT AFT COMPRESSOR 4H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825266 |  | 10301358 | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
305 | KIPP12 | 12MBA80CP054 | P AFT COMPRESSOR 8H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 | 9825267 |  | 10301359 | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
306 | KIPP12 | 12MBE41CP013 | GT H/F WATER PUMP SUCTION FILTER PDT |  |  |  | -1000 | 2200 | mBar | ROSEMOUNT | 2088TG | 2753519 |  | 10301360 | ZM06
307 | KIPP12 | 12MBE41CP121 | GT H/F WATER PUMP-1 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210447
308 | KIPP12 | 12MBE41CP122 | GT H/F WATER PUMP-2 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210453
309 | KIPP12 | 12MBE41CP123 | GT H/F WATER PUMP-3 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 10195290
310 | KIPP12 | 12MBE41CP124 | GT H/F WATER PUMP-4 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 10195289
311 | KIPP12 | 12MBE41CP141 | GT H/F WATER PUMP-1 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631491
312 | KIPP12 | 12MBE41CP142 | GT H/F WATER PUMP-2 DISCHARGE PT |  | -14.7 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631489
313 | KIPP12 | 12MBE41CP143 | GT H/F WATER PUMP-3 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631490
314 | KIPP12 | 12MBE41CP144 | GT H/F WATER PUMP-4 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631487
315 | KIPP12 | 12MBH20CP007 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825271 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
316 | KIPP12 | 12MBH20CP008 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825272 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
317 | KIPP12 | 12MBH20CP009 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825273 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
318 | KIPP12 | 12MBH30CL001 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER |  | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313553
319 | KIPP12 | 12MBH30CL002 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER |  | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313554
320 | KIPP12 | 12MBH30CP003 | P SEV COMBUSTOR PLENUM/KA01 |  | -137.89 | 137.89 | 0 | 25 | Bar | YOKOGAWA | 3051 | 9825268 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
321 | KIPP12 | 12MBH30CP004 | P SEV COMBUSTOR PLENUM/KA01 |  | 137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825269 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
322 | KIPP12 | 12MBH30CP005 | P SEV COMBUSTOR PLENUM/KA01 |  | 137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825270 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
323 | KIPP12 | 12MBH30CP015 | PRESSURE DIFF ACROSS LP AIR COOLER |  | -20.684 | 20.684 | 0 | 4 | Bar | ROSEMOUNT | 3051 | 9824812
324 | KIPP12 | 12MBH30CP020 | P QUENSCH WATER TO LP COOLER |  | 137.89 | 137.89 | 0 | 30 | Bar | ROSEMOUNT | 3051 | 9825289
325 | KIPP12 | 12MBH30CP021 | DP SEV COMBUSTOR LINER |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825279 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
326 | KIPP12 | 12MBH30CP022 | P DIFF SEV COMBUSTOR LINER/KA01 |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825277 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
327 | KIPP12 | 12MBH30CP023 | P DIFF SEV COMBUSTOR LINER/KA01 |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825278 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
328 | KIPP12 | 12MBH40CL001 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER |  | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313551
329 | KIPP12 | 12MBH40CL002 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER |  | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313552
330 | KIPP12 | 12MBH40CP015 | DP HP OTC |  | -621.6 | 621.6 | 0 | 500 | mBar | ROSEMOUNT | 3051 PT | 9825291
331 | KIPP12 | 12MBH41CP102 | PRESSURE AFTER BLOW-OFF BYPASS VALVE |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CD
332 | KIPP12 | 12MBH41CP103 | DP FLOW MEASUREMENT |  | -20.684 | 20.684 | 0 | 10 | Bar | ROSEMOUNT | 3051CD
333 | KIPP12 | 12MBH52CP001 | EXHAUST BEARING FAN 1 PDI |  | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891375
334 | KIPP12 | 12MBH52CP002 | EXHAUST BEARING FAN 2 PDI |  | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891376
335 | KIPP12 | 12MBH60CP001 | DP CMAS FAN 1 |  | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891373
336 | KIPP12 | 12MBH60CP002 | DP CMAS FAN 2 |  | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891374
337 | KIPP12 | 12MBH80CP011 | DIFFERENTIAL PRESSURE EV COMBUSTOR |  | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825282
338 | KIPP12 | 12MBH80CP012 | DIFFERENTIAL PRESSURE EV COMBUSTOR |  | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825283
339 | KIPP12 | 12MBH90CP001 | PRESSURE BEFORE ANTI-ICING CONTROL VALVE |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914215
340 | KIPP12 | 12MBH90CP004 | DP OVER ANTI ICING CV |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914217
341 | KIPP12 | 12MBL01CP011 | DP AIR INTK FLTR TOT |  | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 98426871
342 | KIPP12 | 12MBL01CP012 | DP AIR INTK FLTR TOT |  | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 9844814
343 | KIPP12 | 12MBL51CP001 | DP PRE FLTR STAGE |  | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844808
344 | KIPP12 | 12MBL51CP002 | DP FINE FLTR STAGE |  | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844809
345 | KIPP12 | 12MBL51CP012 | DP FINE FLTR STAGE |  | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844810
346 | KIPP12 | 12MBL61CP010 | EVAP COOLER PUMP AFTER PRESSURE |  | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9852955
347 | KIPP12 | 12MBP01CP003 | FUEL GAS FILTER DP |  | -2.4864 | 2.4864 | 0 | 1.5 | Bar | ROSEMOUNT | 3051 PT | 9789263
348 | KIPP12 | 12MBP05CP102 | EV FUEL GAS FLOW PT |  | 0 | 55.16 | 0 | 55 | Bar | ROSEMOUNT | 3051 PT | 9846442
349 | KIPP12 | 12MBP41CP001 | P AFT TRIP SOV EV |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782037
350 | KIPP12 | 12MBP41CP004 | DP CV EV STG2 |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782043
351 | KIPP12 | 12MBP41CP006 | P AFT CV FGAS EV |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782038
352 | KIPP12 | 12MBP42CP001 | P BEF FGAS TRIP SOV SEV |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782039
353 | KIPP12 | 12MBP42CP004 | DP CV FGAS SEV |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782044
354 | KIPP12 | 12MBP42CP006 | P AFT CV FGAS SEV |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782040
355 | KIPP12 | 12MBP43CP001 | P BFR CV EV STG1 FGAS |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782041
356 | KIPP12 | 12MBP43CP004 | DP CV EVSTG1 FGAS |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782045
357 | KIPP12 | 12MBP43CP006 | P AFT CV EV STG1 FGAS |  | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782042
358 | KIPP12 | 12MBV10CP001 | PRESSURE LUBE OIL TANK |  | -62.16 | 62.16 | 0 | 60 | Bar | ROSEMOUNT | 3051 PT | 9782022
359 | KIPP12 | 12MBV21CP001 | P AFT LUBE OIL PMP 1 |  | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791825
360 | KIPP12 | 12MBV21CP002 | P AFT LUBE OIL PMP 2 |  | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791826
361 | KIPP12 | 12MBV21CP003 | LUBE OIL FILTER DP |  | -2.4864 | 2.4864 | -2.5 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9782023
362 | KIPP12 | 12MBV22CP001 | EMERGENCY LUBE OIL PUMP AFTER PRESSURE |  | -10.342 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791827
363 | KIPP12 | 12MBV40CP001 | LUBE OIL HEADER PRESSURE |  | -10.342 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791828
364 | KIPP12 | 12MBV40CP002 | LUBE OIL HEADER PRESSURE |  | -10.342 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791829
365 | KIPP12 | 12MBV40CP003 | LUBE OIL HEADER PRESSURE |  | -10.342 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791830
366 | KIPP12 | 12MBV40CP006 | P LUBE OIL HEADER 6 ( PRESSURE SWITCH ) |  | 0 | 10 | 1.99 | 2.2 | Bar | Trafog | Switch | -
367 | KIPP12 | 12MBX21CP001 | P AFT PWR OIL PMP 1 |  | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791831
368 | KIPP12 | 12MBX21CP002 | P AFT PWR OIL PMP 2 |  | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791832
369 | KIPP12 | 12MBX21CP010 | GT P/O TWIN FILTER PDT |  | -20.684 | 20.684 | -2 | 8 | Bar | ROSEMOUNT | 3051CD | 9782046
370 | KIPP12 | 12MBX42CP001 | P HYDR SAFETY SYS |  | -137.89 | 137.89 | 0 | 60 | Bar | ROSEMOUNT | 3051 PT | 9782047
371 | KIPP12 | 12LAB90CP001 | FEED WATER TO GT OTC STRAINER PDT |  | -5 | 5 | 0 | 2 | Bar | YOKOGAWA | EJA110E | 91S313546
372 | KIPP12 | 12LAB91CF101 | FW LP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816774
373 | KIPP12 | 12LAB91CF102 | FW LP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816937
374 | KIPP12 | 12LAB92CF101 | FW HP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816776
375 | KIPP12 | 12LAB92CF102 | FW HP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816777
376 | KIPP11 | 11HAC25CF002 | IP DRUM FW FLOW A | 2026-04-01 | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT |  |  | 10302924 | ZM06 |  |  |  |  | Fluke 754 Multifunction Process Calibrator | 2024-01-04 | Beamex Calibration Pressure Pump 0 - 20 Bar | - | Fluke 750PD5 Dual Range Pressure Module -1+2 Bar | 2024-01-04 | 0
377 | KIPP11 | 11HAC25CF003 | IP DRUM FW FLOW B | 2026-04-01 | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT |  |  | 10302973 | ZM06 |  |  |  |  | Fluke 754 Multifunction Process Calibrator | 2024-01-04 | Beamex Calibration Pressure Pump 0 - 20 Bar | - | Fluke 750PD5 Dual Range Pressure Module -1+2 Bar | 2024-01-04 | 0

## Backup202604_06
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
No | Group | Functional Location | Description | Calibration Date | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No. | Tx Status | SAP Ekipman Kodu | Order Type | SAP Status | Full Model Number | Panel KKS | Comments
1 | KIPP00 | 00GHC01CP101 | DEMIN WATER PUMP-A SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313262 |  |  | ZM06
2 | KIPP00 | 00GHC01CP102 | DEMIN WATER PUMP-A SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313090 |  |  | ZM06
3 | KIPP00 | 00GHC02CP101 | DEMIN WATER PUMP-B SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313263 |  |  | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
4 | KIPP00 | 00GHC02CP102 | DEMIN WATER PUMP-B SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313091 |  |  | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
5 | KIPP00 | 00GHC03CP101 | DEMIN WATER PUMP-C SUCTION PRESS. |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313264 |  |  | ZM06 |  |  | 10LAA00GH101 | Atm. Basıncı 0,935 Bar
6 | KIPP00 | 00GHC03CP102 | DEMIN WATER PUMP-C SUCTION FILTER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313092 |  |  | ZM06 |  |  | 10LAB01GH101
7 | KIPP00 | 00GHC04CP101 | EMERGENCY M/U PUMP-A SUCTION PT |  | -1 | 100 | -1 | 5 | Bar | YOKOGAWA | EJA530E | 91S313216 |  |  | ZM06 |  |  | 10LAB02GH101
8 | KIPP00 | 00GHC04CP102 | EMERGENCY M/U PUMP-A SUCTION STRAINER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313106 |  |  | ZM06 |  |  | 10LAB02GH101
9 | KIPP00 | 00GHC05CP101 | EMERGENCY M/U PUMP-B SUCTION PT |  | -1 | 100 | -1 | 5 | Bar | YOKOGAWA | EJA530E | 91S313214 |  |  | ZM06 |  |  | 10LAB06GH101
10 | KIPP00 | 00GHC05CP102 | EMERGENCY M/U PUMP-B SUCTION STRAINER DP |  | -5000 | 5000 | 0 | 1500 | mBar | YOKOGAWA | EJA110E | 91S313105 |  |  | ZM06 |  |  | 10LAB06GH101
11 | KIPP00 | 00GHC10CP101 | DEMIN. WATER SUPPLY PUMP DISC. PRESS. A | 2026-01-29 | -1 | 20 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313246 |  |  | ZM06 |  |  | 10LAB06GH101
12 | KIPP00 | 00GHC10CP102 | DEMIN. WATER SUPPLY PUMP DISC. PRESS. B | 2026-01-29 | -1 | 20 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313247 |  |  | ZM06 |  |  | 10LAB10GH101
13 | KIPP00 | 00GHC16CP101 | EMERGENCY M/U DISCAHARGE PT - A |  | -1 | 100 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313302 |  |  | ZM06 |  |  | 10LAB10GH101
14 | KIPP00 | 00GHC16CP102 | EMERGENCY M/U DISCAHARGE PT - B |  | -1 | 100 | 0 | 15 | Bar | YOKOGAWA | EJA530E | 91S313303 |  |  | ZM06 |  |  | 10LAB01GH101
15 | KIPP00 | 00GHC24CF101 | CONDENSER MAKE UP WATER FIT |  | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313065 |  |  | ZM06 |  |  | 10LAB02GH101
16 | KIPP00 | 00GKB21CP101 | POTABLE WATER SUPPLY PUMP-A SUCTION PT |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313267 |  |  | ZM06 |  |  | 00GKB21GH01
17 | KIPP00 | 00GKB22CP101 | POTABLE WATER SUPPLY PUMP-B SUCTION PT |  | -1 | 20 | -1 | 4 | Bar | YOKOGAWA | EJA530E | 91S313268 |  |  | ZM06 |  |  | 00GKB21GH01
18 | KIPP00 | 00GKB30CP101 | POTABLE WATER SUPPLY PUMP DISCHARGE PT - A |  | -1 | 20 | 0 | 9 | Bar | YOKOGAWA | EJA530E | 91S313244 |  |  | ZM06 |  |  | 00GKB21GH01
19 | KIPP00 | 00GKB30CP102 | POTABLE WATER SUPPLY PUMP DISCHARGE PT - B |  | -1 | 20 | 0 | 9 | Bar | YOKOGAWA | EJA530E | 91S313245 |  |  | ZM06 |  |  | 00GKB21GH01
20 | KIPP10 | 10LAA00CL101 | DEAERATOR & FW STORAGE TANK LEVEL A |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313099 |  |  | ZM06 |  |  | 10LAB15GH101
21 | KIPP10 | 10LAA00CL102 | DEAERATOR & FW STORAGE TANK LEVEL B |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313098 |  |  | ZM06 |  |  | 10LAB15GH101
22 | KIPP10 | 10LAA00CL103 | DEAERATOR & FW STORAGE TANK LEVEL C |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313095 |  |  | ZM06 |  |  | 10LAB10GH101
23 | KIPP10 | 10LAA00CL104 | DEAERATOR & FW STORAGE TANK LEVEL D |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313094 |  |  | ZM06 |  |  | 10LAB10GH101
24 | KIPP10 | 10LAA00CL105 | DEAERATOR & FW STORAGE TANK LEVEL E |  | -10197.2 | 10197.2 | -2700 | 0 | mmH2O | YOKOGAWA | EJA110E | 91S313093 |  |  | ZM06 |  |  | 10LAB01GH101
25 | KIPP10 | 10LAA00CP101 | DEAERATOR & FW STORAGE TANK PRESSURE A |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313278 |  |  | ZM06 |  |  | 10LAB02GH101
26 | KIPP10 | 10LAA00CP102 | DEAERATOR & FW STORAGE TANK PRESSURE B |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313279 |  |  | ZM06 |  |  | 10LAB02GH101
27 | KIPP10 | 10LAA00CP103 | DEAERATOR & FW STORAGE TANK PRESSURE C |  | -1 | 20 | 0 | 7 | Bar | YOKOGAWA | EJA530E | 91S313280 |  |  | ZM06 |  |  | 10LAB02GH101
28 | KIPP10 | 10LAB01CP102 | STG 10 BOILER FWP C SUCTION PRESSURE |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213232 |  |  | ZM06
29 | KIPP10 | 10LAB02CP102 | BOILER FEED WATER PUMP B SUCTION PT |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213233 |  |  | ZM06
30 | KIPP10 | 10LAB03CP102 | STG 10 BOILER FWP C SUCTION PRESSURE |  | -1 | 20 | 0 | 5 | Bar | YOKOGAWA | EJA530E | 91S213234 |  |  | ZM06
31 | KIPP10 | 10LAB06CP102 | CPH PUMP-A SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313235 |  |  | ZM06
32 | KIPP10 | 10LAB07CP102 | CPH PUMP-B SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313236 |  |  | ZM06
33 | KIPP10 | 10LAB08CP102 | CPH PUMP-C SUCTION PRESS. |  | -1 | 20 | 0 | 6 | Bar | YOKOGAWA | EJA530E | 91S313237 |  |  | ZM06
34 | KIPP10 | 10LAB10CP101 | BOILER FEED WATER PUMP-A HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S313320 |  |  | ZM06 |  |  | 10LAB10GH101
35 | KIPP10 | 10LAB10CP102 | BOILER FEED WATER PUMP-B HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S313321 |  |  | ZM06 |  |  | 10LAB10GH101
36 | KIPP10 | 10LAB11CF101 | BOILER FEED WATER PUMP A HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313539 |  |  | ZM06
37 | KIPP10 | 10LAB11CF102 | BOILER FEED WATER PUMP A HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313542 |  |  | ZM06
38 | KIPP10 | 10LAB11CP101 | BOILER FEED WATER PUMP-A HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213317 |  |  | ZM06
39 | KIPP10 | 10LAB12CF101 | BOILER FEED WATER PUMP B HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313540 |  |  | ZM06
40 | KIPP10 | 10LAB12CF102 | BOILER FEED WATER PUMP B HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313543 |  |  | ZM06
41 | KIPP10 | 10LAB12CP101 | BOILER FEED WATER PUMP-B HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213318 |  |  | ZM06
42 | KIPP10 | 10LAB13CF101 | BOILER FEED WATER PUMP C HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313541 |  |  | ZM06
43 | KIPP10 | 10LAB13CF102 | BOILER FEED WATER PUMP C HP DISCHARGE FT |  | -50986 | 50986 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313544 |  |  | ZM06
44 | KIPP10 | 10LAB13CP101 | BOILER FEED WATER PUMP-C HP DISCHARGE PT |  | -1 | 500 | 0 | 218 | Bar | YOKOGAWA | EJA530E | 91S213319 |  |  | ZM06
45 | KIPP10 | 10LAB15CP101 | CPH PUMP DISCHARGE LINE PT A |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313311 |  |  | ZM06
46 | KIPP10 | 10LAB15CP102 | CPH PUMP DISCHARGE LINE PT B |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313312 |  |  | ZM06
47 | KIPP10 | 10LAB16CP101 | CPH PUMP-A DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S213304 |  |  | ZM06
48 | KIPP10 | 10LAB17CP101 | CPH PUMP-B DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313305 |  |  | ZM06
49 | KIPP10 | 10LAB18CP101 | CPH PUMP-C DISCHARGE PRESS. |  | -1 | 100 | 0 | 39 | Bar | YOKOGAWA | EJA530E | 91S313306 |  |  | ZM06
50 | KIPP10 | 10LAB24CF101 | CRH STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 2500 | mmH2O | YOKOGAWA | EJA110E | 91S313064 |  |  | ZM06
51 | KIPP10 | 10LAB30CP101 | BOILER FEED WATER PUMP IP DISCHARGE PT-A |  | -1 | 500 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313218 |  |  | ZM06 |  |  | 10LAB10GH101
52 | KIPP10 | 10LAB30CP102 | BOILER FEED WATER PUMP IP DISCHARGE PT-B |  | -1 | 500 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313220 |  |  | ZM06 |  |  | 10LAB10GH101
53 | KIPP10 | 10LAB31CP101 | BFWP A IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313299 |  |  | ZM06
54 | KIPP10 | 10LAB32CP101 | BFWP B IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313300 |  |  | ZM06
55 | KIPP10 | 10LAB33CP101 | BFWP C IP DISCHARGE PRESS. |  | -1 | 100 | 0 | 81 | Bar | YOKOGAWA | EJA530E | 91S313301 |  |  | ZM06
56 | KIPP10 | 10LBA10CP001 | P LP STEAM BFR ST | 2026-03-23 | -1 | 20 | -1 | 10 | Bar | YOKOGAWA | EJA530E | 91S313251 |  |  | ZM06
57 | KIPP10 | 10LBA10CP002 | P LP STEAM BFR ST | 2026-03-23 | -1 | 20 | -1 | 10 | Bar | YOKOGAWA | EJA530E | 91S313252 |  |  | ZM06
58 | KIPP10 | 10LBA50CP001 | P HP STEAM BFR ST | 2026-03-18 | -1 | 500 | -1 | 150 | Bar | YOKOGAWA | EJA530E | 91S313322 |  |  | ZM06 |  |  | STG BINASI ZEMIN
59 | KIPP10 | 10LBA50CP002 | P HP STEAM BFR ST | 2026-03-18 | -1 | 500 | -1 | 150 | Bar | YOKOGAWA | EJA530E | 91S313323 |  |  | ZM06 |  |  | STG BINASI ZEMIN
60 | KIPP10 | 10LBB41CP001 | P IP STEAM BFR ST | 2026-03-18 | -1 | 100 | -1 | 40 | Bar | YOKOGAWA | EJA530E | 91S313307 |  |  | ZM06
61 | KIPP10 | 10LBB42CP001 | P IP STEAM BFR ST | 2026-03-18 | -1 | 100 | -1 | 40 | Bar | YOKOGAWA | EJA530E | 91S313308 |  |  | ZM06
62 | KIPP10 | 10LBC10CP001 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313289 |  |  | ZM06
63 | KIPP10 | 10LBC10CP002 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313290 |  |  | ZM06
64 | KIPP10 | 10LBC10CP003 | P CLD RH STEAM AFT ST | 2026-03-18 | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313291 |  |  | ZM06
65 | KIPP10 | 10LBC10CP101 | STG 10 COLD REHEAT STEAM PRESS. | 2026-03-18 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313286 |  |  | ZM06
66 | KIPP10 | 10LBG00CP101 | AUXILIARY STEAM LINE PRESS. | 2026-03-23 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313292 |  |  | ZM06
67 | KIPP10 | 10LBG00CP102 | AUXILIARY STEAM LINE PRESS. | 2026-03-23 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313293 |  |  | ZM06
68 | KIPP10 | 10LCA01CP102 | CONDENSATE EXTRACTION PUMP-A SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313253 |  |  | ZM06
69 | KIPP10 | 10LCA02CP102 | CONDENSATE EXTRACTION PUMP-B SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313254 |  |  | ZM06
70 | KIPP10 | 10LCA03CP102 | CONDENSATE EXTRACTION PUMP-C SUCTION PT |  | -1 | 20 | -1 | 3 | Bar | YOKOGAWA | EJA530E | 91S313255 |  |  | ZM06
71 | KIPP10 | 10LCA10CF101 | CONDENSATE EXTRACTION PUMP DISCHARGE FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313066 |  |  | ZM06
72 | KIPP10 | 10LCA10CF102 | CONDENSATE EXTRACTION PUMP DISCHARGE FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313101 |  |  | ZM06
73 | KIPP10 | 10LCA10CP101 | CONDENSATE EXTRACTION PUMP DISCHARGE PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313297 |  |  | ZM06
74 | KIPP10 | 10LCA10CP102 | GLAND STEAM CONDENSER OUTLET PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313298 |  |  | ZM06
75 | KIPP10 | 10LCA10CP103 | CONDENSATE EXTRACTION PUMP DISCHARGE PT | 2026-03-24 | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313310 |  |  | ZM06
76 | KIPP10 | 10LCA11CP101 | CEP-A DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313294 |  |  | ZM06
77 | KIPP10 | 10LCA12CP101 | CEP-B DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313295 |  |  | ZM06
78 | KIPP10 | 10LCA13CP101 | CEP-C DISCHARGE PRESS. |  | -1 | 100 | 0 | 35 | Bar | YOKOGAWA | EJA530E | 91S313296 |  |  | ZM06
79 | KIPP10 | 10LCA20CF101 | DEAERATOR & FW STORAGE TANK INLET FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313069 |  |  | ZM06
80 | KIPP10 | 10MAA10CP001 | P UPSTR HPT BLADING |  | -1.013 | 275.789 | -1 | 150 | Bar | ROSEMOUNT | 3051 PT | 9834864 |  |  | ZM06
81 | KIPP10 | 10MAB10CP001 | P UPSTR IPT BLADING |  | -137.89 | 137.89 | -1 | 40 | Bar | ROSEMOUNT | 3051 PT | 9834862 |  |  | ZM06
82 | KIPP10 | 10MAB10CP002 | P UPSTR IPT BLADING |  | -137.89 | 137.89 | -1 | 40 | Bar | ROSEMOUNT | 3051 PT | 9834863 |  |  | ZM06
83 | KIPP10 | 10MAC01CP021 | LP TUR.UPER STR.CROSS PIPE PRESSURE |  | -20.684 | 20.684 | -1 | 8 | Bar | ROSEMOUNT | 3051 PT | 9834860 |  |  | ZM06
84 | KIPP10 | 10MAC01CP022 | LP TUR.UPER STR.CROSS PIPE PRESSURE |  | -20.684 | 20.684 | -1 | 8 | Bar | ROSEMOUNT | 3051 PT | 9834861 |  |  | ZM06
85 | KIPP10 | 10MAC10CP031 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861934 |  |  | ZM06
86 | KIPP10 | 10MAC10CP032 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861935 |  |  | ZM06
87 | KIPP10 | 10MAC10CP033 | LP TURBINE EXHAUST PRESSURE |  | 0 | 2068.4 | 0 | 1200 | mBar | ROSEMOUNT | 3051 PT | 9861936 |  |  | ZM06
88 | KIPP10 | 10MAV40CP003 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843509 |  |  | ZM06
89 | KIPP10 | 10MAV40CP004 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843508 |  |  | ZM06
90 | KIPP10 | 10MAV40CP005 | P LOIL HEADER |  | -1.0132 | 10.3421 | 0 | 6 | Bar | ROSEMOUNT | 3051 PT | 9843510 |  |  | ZM06
91 | KIPP10 | 10MAW02CP001 | GLAND STEAM LINE PT |  | -1 | 100 | -1 | 50 | Bar | YOKOGAWA | EJA530E | 91S313309 |  |  | ZM06
92 | KIPP10 | 10MAW15CP001 | GLAND STEAM SEALING SYSTEM PRESSURE |  | -2486.4 | 2486.4 | -150 | 350 | mBar | ROSEMOUNT | 3051 PT | 9834859 |  |  | ZM06
93 | KIPP10 | 10MAX11CP031 | P HYDR HEADER |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843512 |  |  | ZM06
94 | KIPP10 | 10MAX44CP001 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843513 |  |  | ZM06
95 | KIPP10 | 10MAX44CP002 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843511 |  |  | ZM06
96 | KIPP10 | 10MAX44CP003 | P SAFETY SYSTEM |  | -1.013 | 275.789 | 0 | 52 | Bar | ROSEMOUNT | 3051 PT | 9843514 |  |  | ZM06
97 | KIPP10 | 10MKA13CP111 | GEN.AIR BLOWER FILTER PRESSURE |  | -1013.2 | 2068.4 | -50 | 0 | mBar | ROSEMOUNT | 2088 PT | 9917083 |  |  | ZM06
98 | KIPP10 | 10MKA13CP112 | GEN.AIR BLOWER AFTER FAN PRESSURE |  | -1013.2 | 2068.4 | 0 | 400 | mBar | ROSEMOUNT | 2088 PT | 9917081 |  |  | ZM06
99 | KIPP10 | 10MKA13CP113 | GEN.AIR BLOWER AFTER FAN PRESSURE |  | -1013.2 | 2068.4 | 0 | 400 | mBar | ROSEMOUNT | 2088 PT | 9917082 |  |  | ZM06
100 | KIPP11 | 11EKG40CP101 | FG PERFORMANCE HEATER SKID OUTLET PRESS |  | -1 | 100 | 0 | 61 | Bar | YOKOGAWA | EJA530E | 91S313313 |  |  | ZM06
101 | KIPP11 | 11HAC22CF002 | LP FW FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214472 |  |  | ZM06 |  |  | 11LAB46GH101
102 | KIPP11 | 11HAC22CF003 | LP FW FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214473 |  |  | ZM06 |  |  | 11LAB46GH101
103 | KIPP11 | 11HAC25CF002 | IP DRUM FW FLOW A | 2026-04-01 | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214462 |  |  | ZM06 |  |  | 11HAC25GH101
104 | KIPP11 | 11HAC25CF003 | IP DRUM FW FLOW B | 2026-04-01 | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214467 |  |  | ZM06 |  |  | 11HAC25GH101
105 | KIPP11 | 11HAC25CP001 | IP ECO O/L PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051TG | 210426 |  |  | ZM06 |  |  | 11HAC25GH101
106 | KIPP11 | 11HAC58CF002 | HP ECO O/L FT 1 |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214452 |  |  | ZM06 |  |  | 11HAC58GH101
107 | KIPP11 | 11HAC58CF003 | HP ECO O/L FT 2 |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214453 |  |  | ZM06 |  |  | 11HAC58GH101
108 | KIPP11 | 11HAC58CP001 | HP ECO O/L PT |  | 0 | 689.7 | 0 | 300 | Bar | ROSEMOUNT | 2050 TG | 210420 |  |  | ZM06 |  |  | 11HAC58GH101
109 | KIPP11 | 11HAD10CL001 | LP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576009 |  |  | ZM06 |  |  | 11HAC25GH101
110 | KIPP11 | 11HAD10CL002 | LP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576010 |  |  | ZM06 |  |  | 11HAD50GH102
111 | KIPP11 | 11HAD10CL003 | LP DRUM LT 3 | 3.04.2026 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576011 |  |  | ZM06 |  |  | 11HAD50GH102
112 | KIPP11 | 11HAD10CP001 | LP DRUM PT 1 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576027 |  |  | ZM06 |  |  | 11HAD30GH101
113 | KIPP11 | 11HAD10CP002 | LP DRUM PT 2 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576028 |  |  | ZM06 |  |  | 11HAD30GH101
114 | KIPP11 | 11HAD10CP003 | LP DRUM PT 3 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576029 |  |  | ZM06 |  |  | 11HAD30GH101
115 | KIPP11 | 11HAD30CL001 | IP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576006 |  |  | ZM06 |  |  | 11HAC25GH101
116 | KIPP11 | 11HAD30CL002 | IP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576007 |  |  | ZM06 |  |  | 11HAD50GH102
117 | KIPP11 | 11HAD30CL003 | IP DRUM LT 3 | 2026-04-03 | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576008 |  |  | ZM06 |  |  | 11HAD50GH102
118 | KIPP11 | 11HAD30CP001 | IP DRUM PT 1 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575997 |  |  | ZM06 |  |  | 11HAD30GH101
119 | KIPP11 | 11HAD30CP002 | IP DRUM PT 2 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575998 |  |  | ZM06 |  |  | 11HAD30GH101
120 | KIPP11 | 11HAD30CP003 | IP DRUM PT 3 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3575999 |  |  | ZM06 |  |  | 11HAD30GH101
121 | KIPP11 | 11HAD50CL001 | HP DRUM LT 1 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576004 |  |  | ZM06 |  |  | 11HAC25GH101
122 | KIPP11 | 11HAD50CL002 | HP DRUM LT 2 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576003 |  |  | ZM06 |  |  | 11HAD50GH102
123 | KIPP11 | 11HAD50CL003 | HP DRUM LT 3 | 2026-04-03 | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576005 |  |  | ZM06 |  |  | 11HAD50GH102
124 | KIPP11 | 11HAD50CP001 | HP DRUM PT 1 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575991 |  |  | ZM06 |  |  | 11HAD50GH101
125 | KIPP11 | 11HAD50CP002 | HP DRUM PT 2 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575992 |  |  | ZM06 |  |  | 11HAD50GH101
126 | KIPP11 | 11HAD50CP003 | HP DRUM PT 3 | 2026-04-01 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575993 |  |  | ZM06 |  |  | 11HAD50GH101
127 | KIPP11 | 11LAB20CF101 | HP STEAM BYPASS SPRAYAY WATER FT |  | -6350 | 6350 | 0 | 6300 | mmH2O | ROSEMOUNT | 2051 PT | 214447 |  |  | ZM06
128 | KIPP11 | 11LAB31CF101 | FEED WATER FROM CONDENSATE PREHEATER FT |  | -10197.2 | 10197.2 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313068 |  |  | ZM06 |  |  | 10LAB10GH101
129 | KIPP11 | 11LAB46CP001 | IP/LP FW PT | 2026-04-02 | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051 PT | 210430 |  |  | ZM06 |  |  | 11LAB46GH101
130 | KIPP11 | 11LAB90CP001 | FEED WATER TO GT OTC STRAINER PDT |  | -5 | 5 | 0 | 2 | Bar | YOKOGAWA | EJA110E | 91S313545 |  |  | ZM06
131 | KIPP11 | 11LAB91CF101 | FW LP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816770 |  |  | ZM06
132 | KIPP11 | 11LAB91CF102 | FW LP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816771 |  |  | ZM06
133 | KIPP11 | 11LAB92CF101 | FW HP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816772 |  |  | ZM06
134 | KIPP11 | 11LAB92CF102 | FW HP OTC FITCA |  | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816773 |  |  | ZM06
135 | KIPP11 | 11LAB96CP001 | HP FW PT | 2026-04-02 | 0 | 289.3 | 0 | 300 | Bar | ROSEMOUNT | 2051 PT | 210424 |  |  | ZM06 |  |  | 11LAB96GH101
136 | KIPP11 | 11LAE50CF002 | HP DESUPERHEATER SPRAY FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214454 |  |  | ZM06 |  |  | 11LAE50GH101
137 | KIPP11 | 11LAE50CF003 | HP DESUPERHEATER SPRAY FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214455 |  |  | ZM06 |  |  | 11LAE50GH101
138 | KIPP11 | 11LAF40CF002 | RH DESUPERHEATER SPRAY FT 1 | 2026-04-01 | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214468 |  |  | ZM06 |  |  | 11LAB46GH101
139 | KIPP11 | 11LAF40CF003 | RH DESUPERHEATER SPRAY FT 2 | 2026-04-01 | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214469 |  |  | ZM06 |  |  | 11LAB46GH101
140 | KIPP11 | 11LBA00CP101 | HP STEAM PRESSURE | 2026-03-17 | -1 | 500 | 0 | 151 | Bar | YOKOGAWA | EJA530E | 91S313315 |  |  | ZM06 |  |  |  | Set: 2,2 - Reset: 1,99
141 | KIPP11 | 11LBA10CF002 | LP STEAM O/L FT 1 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214474 |  |  | ZM06 |  |  | 11LAB96GH101
142 | KIPP11 | 11LBA10CF003 | LP STEAM O/L FT 2 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214475 |  |  | ZM06 |  |  | 11LAB96GH101
143 | KIPP11 | 11LBA10CP001 | LP STEAM PRESSURE | 2026-03-24 | -1 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 210437 |  |  | ZM06 |  |  | 11LAB96GH101
144 | KIPP11 | 11LBA20CP101 | HP BYPASS VALVE OUTLET PRESSURE A | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313282 |  |  | ZM06
145 | KIPP11 | 11LBA20CP102 | HP BYPASS VALVE OUTLET PRESSURE B | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313283 |  |  | ZM06
146 | KIPP11 | 11LBA30CF002 | IP STEAM O/L FT 1 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214470 |  |  | ZM06 |  |  | 11LBA30GH101
147 | KIPP11 | 11LBA30CF003 | IP STEAM O/L FT 2 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214471 |  |  | ZM06 |  |  | 11LBA30GH101
148 | KIPP11 | 11LBA30CP001 | IP STEAM O/L PT |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210431 | [5 empty] | 11LBA30GH101
149 | KIPP11 | 11LBA31CP101 | LP STEAM PT | 2026-03-24 | -1 | 20 | 0 | 10 | Bar | YOKOGAWA | EJA530E | 91S313226
150 | KIPP11 | 11LBA40CP101 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313227
151 | KIPP11 | 11LBA40CP102 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313228
152 | KIPP11 | 11LBA50CF002 | HP STEAM O/L FT 1 | 2026-04-02 | -2486 | 2486 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214456 |  |  | ZM06 |  |  | 11LBC00GH101
153 | KIPP11 | 11LBA50CF003 | HP STEAM O/L FT 2 | 2026-04-02 | -2486 | 2486 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214457 |  |  | ZM06 |  |  | 11LBC00GH101
154 | KIPP11 | 11LBA50CP001 | HP STEAM PT | 2026-04-02 | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 210425 |  |  | ZM06
155 | KIPP11 | 11LBB00CP101 | HOT REHEAT STEAM PT | 2026-03-17 | -1 | 100 | 0 | 50 | Bar | YOKOGAWA | EJA530E | 91S313213
156 | KIPP11 | 11LBB20CP101 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313222
157 | KIPP11 | 11LBB20CP102 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313223 |  |  | ZM06
158 | KIPP11 | 11LBB40CP001 | HOT REHEAT STEAM PT | 2026-04-02 | -1.01 | 275.79 | 0 | 50 | Bar | ROSEMOUNT | 2051 PT | 210432 |  |  | ZM06 |  |  | 11LBA30GH101
159 | KIPP11 | 11LBC00CF101 | COLD REHEAT STEAM FLOW A | 2026-04-02 | -10197.2 | 10197.2 | 0 | 4756.2 | mmH2O | YOKOGAWA | EJA110E | 91S313071 |  |  | ZM06 |  |  | 11LBC00GH101
160 | KIPP11 | 11LBC00CF102 | COLD REHEAT STEAM FLOW B | 2026-04-02 | -10197.2 | 10197.2 | 0 | 4756.2 | mmH2O | YOKOGAWA | EJA110E | 91S313072 |  |  | ZM06 |  |  | 11LBC00GH101
161 | KIPP11 | 11LBC00CP101 | COLD REHEAT STEAM PRESSURE | 2026-04-02 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313287 |  |  | ZM06 |  |  | 11LBC00GH101
162 | KIPP11 | 11LBC30CP001 | COLD REHEAT STEAM PT |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210433 |  |  | ZM06 |  |  | 11HAC58GH101
163 | KIPP11 | 11LBG91CP001 | GT OTC OUT STEAM LINE PT-1 | 2026-04-02 | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S313324 |  |  | ZM06
164 | KIPP11 | 11LBG91CP002 | GT OTC OUT STEAM LINE PT-2 | 2026-04-02 | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S313326 |  |  | ZM06
165 | KIPP11 | 11LCA20CF101 | LP STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313062 |  |  | ZM06
166 | KIPP11 | 11LCA21CF101 | HOT REHEAT STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313060 |  |  | ZM06
167 | KIPP11 | 11MBA30CP001 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824805 |  |  | ZM06
168 | KIPP11 | 11MBA30CP003 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824806 |  |  | ZM06
169 | KIPP11 | 11MBA30CP004 | PRESSURE MEASUREMENT EXHAUST DIFFUSER | 2026-01-19 | 0 | 20.684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824807 |  |  | ZM06
170 | KIPP11 | 11MBA80CP051 | GT AFT COMPRESSOR 1H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825256 |  |  | ZM06
171 | KIPP11 | 11MBA80CP052 | GT AFT COMPRESSOR 4H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825257 |  |  | ZM06
172 | KIPP11 | 11MBA80CP054 | P AFT COMPRESSOR 8H PT | 2026-01-19 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CD | 9825258 |  |  | ZM06
173 | KIPP11 | 11MBE41CP013 | GT H/F WATER PUMP SUCTION FILTER PDT |  | 0 | 0 | -1000 | 2200 | mBar | ROSEMOUNT | 2088TG | 2753518 |  |  | ZM06
174 | KIPP11 | 11MBE41CP121 | GT H/F WATER PUMP-1 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210595 |  |  | ZM06
175 | KIPP11 | 11MBE41CP122 | GT H/F WATER PUMP-2 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210445 |  |  | ZM06
176 | KIPP11 | 11MBE41CP123 | GT H/F WATER PUMP-3 SUCTION PT |  | -14.7 | 800 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210429 |  |  | ZM06
177 | KIPP11 | 11MBE41CP124 | GT H/F WATER PUMP-4 SUCTION PT |  | -14.7 | 4000 | -14.7 | 150 | psi | ROSEMOUNT | 2051TG | 210446 |  |  | ZM06
178 | KIPP11 | 11MBE41CP141 | GT H/F WATER PUMP-1 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631493 |  |  | ZM06
179 | KIPP11 | 11MBE41CP142 | GT H/F WATER PUMP-2 DISCHARGE PT |  | -14.7 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 607375 |  |  | ZM06
180 | KIPP11 | 1: 11MBE41CP143; 2: GT H/F WATER PUMP-3 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631492
181 | KIPP11 | 11MBE41CP144 | GT H/F WATER PUMP-4 DISCHARGE PT |  | 0 | 4000 | -14.7 | 4000 | psi | ROSEMOUNT | 2088TG | 631494 |  |  | ZM06
182 | KIPP11 | 11MBH20CP007 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825262 |  |  | ZM06
183 | KIPP11 | 11MBH20CP008 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825263 |  |  | ZM06
184 | KIPP11 | 11MBH20CP009 | GT CARR COOLING AIR PT | 2026-01-19 | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051CG | 9825264 |  |  | ZM06
185 | KIPP11 | 11MBH30CL001 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-19 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313549 |  |  | ZM06
186 | KIPP11 | 11MBH30CL002 | LP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-19 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313550 |  |  | ZM06
187 | KIPP11 | 11MBH30CP003 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 PT | 9825259 |  |  | ZM06
188 | KIPP11 | 11MBH30CP004 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 PT | 9825260 |  |  | ZM06
189 | KIPP11 | 11MBH30CP005 | P SEV COMBUSTOR PLENUM/KA01 | 2026-01-19 | -137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825261 |  |  | ZM06
190 | KIPP11 | 11MBH30CP015 | PRESSURE DIFF ACROSS LP AIR COOLER | 2026-01-19 | -20.684 | 20.684 | 0 | 4 | Bar | ROSEMOUNT | 3051 PT | 9824811 |  |  | ZM06
191 | KIPP11 | 11MBH30CP020 | P QUENSCH WATER TO LP COOLER | 2026-01-20 | -137.89 | 137.89 | 0 | 30 | Bar | ROSEMOUNT | 3051 PT | 9825287 |  |  | ZM06
192 | KIPP11 | 11MBH30CP021 | GT SEV COMBUSTOR LINER/KA01 PDT | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825276 |  |  | ZM06
193 | KIPP11 | 11MBH30CP022 | P DIFF SEV COMBUSTOR LINER/KA01 | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825274 |  |  | ZM06
194 | KIPP11 | 11MBH30CP023 | P DIFF SEV COMBUSTOR LINER/KA01 | 2026-01-20 | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051CD | 9825275 |  |  | ZM06
195 | KIPP11 | 11MBH40CL001 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-20 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313547 |  |  | ZM06
196 | KIPP11 | 11MBH40CL002 | HP OTC DIFFRENTIAL LEVEL TRANSMITTER | 2026-01-20 | -5 | 5 | 0 | -2 | Bar | YOKOGAWA | EJA110E | 91S313548 |  |  | ZM06
197 | KIPP11 | 11MBH40CP015 | DP HP OTC | 2026-01-20 | -621.6 | 621.6 | 0 | 500 | mBar | ROSEMOUNT | 3051 PT | 9825290 |  |  | ZM06
198 | KIPP11 | 11MBH41CP102 | PRESSURE AFTER BLOW-OFF BYPASS VALVE | 2026-01-20 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CD | 9855800 |  |  | ZM06
199 | KIPP11 | 11MBH41CP103 | DP FLOW MEASUREMENT | 2026-01-20 | -20.684 | 20.684 | 0 | 10 | Bar | ROSEMOUNT | 3051CD | 9855803 |  |  | ZM06
200 | KIPP11 | 11MBH52CP001 | EXHAUST BEARING FAN 1 PDI | 2026-01-20 | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891371 |  |  | ZM06
201 | KIPP11 | 11MBH52CP002 | EXHAUST BEARING FAN 2 PDI | 2026-01-20 | -621.6 | 621.6 | 0 | 400 | mBar | ROSEMOUNT | 3051 PT | 9891372 |  |  | ZM06
202 | KIPP11 | 11MBH60CP001 | DP CMAS FAN 1 | 2026-01-20 | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891369
203 | KIPP11 | 11MBH60CP002 | DP CMAS FAN 2 | 2026-01-20 | -621.6 | 621.6 | 0 | 50 | mBar | ROSEMOUNT | 3051 PT | 9891370 |  |  | ZM06
204 | KIPP11 | 11MBH80CP011 | DIFFERENTIAL PRESSURE EV COMBUSTOR | 2026-01-20 | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825280 |  |  | ZM06
205 | KIPP11 | 11MBH80CP012 | DIFFERENTIAL PRESSURE EV COMBUSTOR | 2026-01-20 | -2.4864 | 2.4864 | 0 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9825281 |  |  | ZM06
206 | KIPP11 | 11MBH90CP001 | PRESSURE BEFORE ANTI-ICING CONTROL VALVE | 2026-01-21 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914214 |  |  | ZM06
207 | KIPP11 | 11MBH90CP004 | DP OVER ANTI ICING CV | 2026-01-21 | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 PT | 9914216 |  |  | ZM06
208 | KIPP11 | 11MBL01CP011 | DP AIR INTK FLTR TOT | 2026-01-21 | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 9844811 |  |  | ZM06
209 | KIPP11 | 11MBL01CP012 | DP AIR INTK FLTR TOT | 2026-01-21 | -621.6 | 621.6 | 0 | 3000 | Pa | ROSEMOUNT | 3051 PT | 9844812 |  |  | ZM06
210 | KIPP11 | 11MBL51CP001 | DP PRE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844805 |  |  | ZM06
211 | KIPP11 | 11MBL51CP002 | DP FINE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844806 |  |  | ZM06
212 | KIPP11 | 11MBL51CP012 | DP FINE FLTR STAGE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051 PT | 9844807 |  |  | ZM06
213 | KIPP11 | 11MBL61CP010 | EVAP COOLER PUMP AFTER PRESSURE | 2026-01-21 | -621.6 | 621.6 | 0 | 2500 | Pa | ROSEMOUNT | 3051CD | 9852954 |  |  | ZM06
214 | KIPP11 | 11MBP01CP003 | FUEL GAS FILTER DP | 2026-01-21 | -2.4864 | 2.4864 | 0 | 1.5 | Bar | ROSEMOUNT | 3051 PT | 9789262 |  |  | ZM06
215 | KIPP11 | 11MBP05CP102 | EV FUEL GAS FLOW PT | 2026-01-21 | 0 | 55.16 | 0 | 55 | Bar | ROSEMOUNT | 3051 PT | 9846441 |  |  | ZM06 |  |  |  | Atm. Basıncı 0,935 Bar
216 | KIPP11 | 11MBP41CP001 | P AFT TRIP SOV EV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782024 |  |  | ZM06
217 | KIPP11 | 11MBP41CP004 | DP CV EV STG2 | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782030 |  |  | ZM06
218 | KIPP11 | 11MBP41CP006 | P AFT CV FGAS EV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782025 |  |  | ZM06
219 | KIPP11 | 11MBP42CP001 | P BEF FGAS TRIP SOV SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782026 |  |  | ZM06
220 | KIPP11 | 11MBP42CP004 | DP CV FGAS SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782031 |  |  | ZM06
221 | KIPP11 | 11MBP42CP006 | P AFT CV FGAS SEV | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782027 |  |  | ZM06
222 | KIPP11 | 11MBP43CP001 | P BFR CV EV STG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782028 |  |  | ZM06
223 | KIPP11 | 11MBP43CP004 | DP CV EVSTG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782032 |  |  | ZM06
224 | KIPP11 | 11MBP43CP006 | P AFT CV EV STG1 FGAS | 2026-01-21 | -137.89 | 137.89 | 0 | 70 | Bar | ROSEMOUNT | 3051 PT | 9782029 |  |  | ZM06
225 | KIPP11 | 11MBV10CP001 | PRESSURE LUBE OIL TANK | 2026-01-22 | -621.6 | 621.6 | 0 | 60 | mBar | ROSEMOUNT | 3051 PT | 9781969 |  |  | ZM06
226 | KIPP11 | 11MBV21CP001 | P AFT LUBE OIL PMP 1 | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791817 |  |  | ZM06
227 | KIPP11 | 11MBV21CP002 | P AFT LUBE OIL PMP 2 | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791818 |  |  | ZM06
228 | KIPP11 | 11MBV21CP003 | LUBE OIL FILTER DP | 2026-01-22 | -2.4864 | 2.4864 | -2.5 | 2.5 | Bar | ROSEMOUNT | 3051 PT | 9781970 |  |  | ZM06
229 | KIPP11 | 11MBV22CP001 | EMERGENCY LUBE OIL PUMP AFTER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791819 |  |  | ZM06
230 | KIPP11 | 11MBV40CP001 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791820 |  |  | ZM06
231 | KIPP11 | 11MBV40CP002 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791821 |  |  | ZM06
232 | KIPP11 | 11MBV40CP003 | LUBE OIL HEADER PRESSURE | 2026-01-22 | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791822 |  |  | ZM06
233 | KIPP11 | 11MBV40CP006 | P LUBE OIL HEADER 6 ( PRESSURE SWITCH ) | 2026-01-22 | 0 | 10 | - | 2.11 | Bar | TRAFOG | Switch | - |  |  | ZM06
234 | KIPP11 | 11MBX21CP001 | P AFT PWR OIL PMP 2 | 2026-01-22 | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791823 |  |  | ZM06
235 | KIPP11 | 11MBX21CP002 | P AFT PWR OIL PMP 1 | 2026-01-22 | -1.01 | 55.16 | 0 | 52 | Bar | ROSEMOUNT | 2088 PT | 9791824 |  |  | ZM06
236 | KIPP11 | 11MBX21CP010 | GT P/O TWIN FILTER PDT | 2026-01-22 | -20.684 | 20.684 | -2 | 8 | Bar | ROSEMOUNT | 3051CD | 9782033 |  |  | ZM06
237 | KIPP11 | 11MBX42CP001 | P HYDR SAFETY SYS | 2026-01-22 | -137.89 | 137.89 | 0 | 60 | Bar | ROSEMOUNT | 3051 PT | 9782034 |  |  | ZM06
238 | KIPP12 | 12EKG40CP101 | FG PERFORMANCE HEATER SKID OUTLET PRESS |  | -1 | 100 | 0 | 61 | Bar | YOKOGAWA | EJA530E | 91S313314 |  |  | ZM06
239 | KIPP12 | 12HAC22CF002 | LP FW FT 1 |  | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214484 |  |  | ZM06 |  |  | 12LAB46GH101
240 | KIPP12 | 12HAC22CF003 | LP FW FT 2 |  | -621.6 | 621.6 | 0 | 316 | mBar | ROSEMOUNT | 2051 PT | 214485 |  |  | ZM06 |  |  | 12LAB46GH101
241 | KIPP12 | 12HAC25CF002 | IP DRUM FW FLOW A |  | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214478 |  |  | ZM06 |  |  | 12HAC25GH101
242 | KIPP12 | 12HAC25CF003 | IP DRUM FW FLOW B |  | -621.6 | 621.6 | 0 | 460 | mBar | ROSEMOUNT | 2051 PT | 214479 |  |  | ZM06 |  |  | 12HAC25GH101
243 | KIPP12 | 12HAC25CP001 | IP ECO O/L PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051TG | 210444 |  |  | ZM06 |  |  | 12HAC25GH101
244 | KIPP12 | 12HAC58CF002 | HP ECO O/L FT 1 |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214463 |  |  | ZM06 |  |  | 12HAC58GH101
245 | KIPP12 | 12HAC58CF003 | HP ECO O/L FT 2 |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 CD | 214464 |  |  | ZM06 |  |  | 12HAC58GH101
246 | KIPP12 | 12HAC58CP001 | HP ECO O/L PT |  | 0 | 689.7 | 0 | 300 | Bar | ROSEMOUNT | 2050TG | 210438 |  |  | ZM06 |  |  | 12HAC58GH101
247 | KIPP12 | 12HAD10CL001 | LP DRUM LT 1 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576021 |  |  | ZM06 |  |  | 12HAC25GH101
248 | KIPP12 | 12HAD10CL002 | LP DRUM LT 2 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576022 |  |  | ZM06 |  |  | 12HAD50GH102
249 | KIPP12 | 12HAD10CL003 | LP DRUM LT 3 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576023 |  |  | ZM06 |  |  | 12HAD50GH102
250 | KIPP12 | 12HAD10CP001 | LP DRUM PT 1 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576030 |  |  | ZM06 |  |  | 12HAD30GH101
251 | KIPP12 | 12HAD10CP002 | LP DRUM PT 2 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576031 |  |  | ZM06 |  |  | 12HAD30GH101
252 | KIPP12 | 12HAD10CP003 | LP DRUM PT 3 |  | -1.01 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 3576032 |  |  | ZM06 |  |  | 12HAD30GH101
253 | KIPP12 | 12HAD30CL001 | IP DRUM LT 1 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576018 |  |  | ZM06 |  |  | 12HAC25GH101
254 | KIPP12 | 12HAD30CL002 | IP DRUM LT 2 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576019 |  |  | ZM06 |  |  | 12HAD50GH102
255 | KIPP12 | 12HAD30CL003 | IP DRUM LT 3 |  | -6350 | 6350 | -34 | -1143 | mmH2O | ROSEMOUNT | 2051 PT | 3576020 |  |  | ZM06 |  |  | 12HAD50GH102
256 | KIPP12 | 12HAD30CP001 | IP DRUM PT 1 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576000 |  |  | ZM06 |  |  | 12HAD30GH101
257 | KIPP12 | 12HAD30CP002 | IP DRUM PT 2 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576001 |  |  | ZM06 |  |  | 12HAD30GH101
258 | KIPP12 | 12HAD30CP003 | IP DRUM PT 3 |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 3576002 |  |  | ZM06 |  |  | 12HAD30GH101
259 | KIPP12 | 12HAD50CL001 | HP DRUM LT 1 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576015 |  |  | ZM06 |  |  | 12HAC25GH101
260 | KIPP12 | 12HAD50CL002 | HP DRUM LT 2 |  | -6350 | 6350 | -39 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576016 |  |  | ZM06 |  |  | 12HAD50GH102
261 | KIPP12 | 12HAD50CL003 | HP DRUM LT 3 |  | -6350 | 6350 | -33 | -1294 | mmH2O | ROSEMOUNT | 2051 PT | 3576017 |  |  | ZM06 |  |  | 12HAD50GH102
262 | KIPP12 | 12HAD50CP001 | HP DRUM PT 1 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575994 |  |  | ZM06 |  |  | 12HAD50GH101
263 | KIPP12 | 12HAD50CP002 | HP DRUM PT 2 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575995 |  |  | ZM06 |  |  | 12HAD50GH101
264 | KIPP12 | 12HAD50CP003 | HP DRUM PT 3 |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 3575996 |  |  | ZM06 |  |  | 12HAD50GH101
265 | KIPP12 | 12LAB20CF101 | HP STEAM BYPASS SPRAYAY WATER FT |  | -6350 | 6350 | 0 | 6300 | mmH2O | ROSEMOUNT | 2051 PT | 214441 |  |  | ZM06
266 | KIPP12 | 12LAB31CF101 | FW FROM CONDENSATE PREHEATER FT |  | -10197.2 | 10197.2 | 0 | 7500 | mmH2O | YOKOGAWA | EJA110E | 91S313067 |  |  | ZM06 |  |  | 10LAB10GH101
267 | KIPP12 | 12LAB46CP001 | IP/LP FW PT |  | -1.01 | 275.79 | 0 | 100 | Bar | ROSEMOUNT | 2051 PT | 210448 |  |  | ZM06 |  |  | 12LAB46GH101
268 | KIPP12 | 12LAB96CP001 | HP FW PT |  | 0 | 689.5 | 0 | 300 | Bar | ROSEMOUNT | 2051 PT | 210442 |  |  | ZM06 |  |  | 12LAB96GH101
269 | KIPP12 | 12LAE50CF002 | HP DESUPERHEATER SPRAY FT 1 |  | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214465 |  |  | ZM06 |  |  | 12LAE50GH101
270 | KIPP12 | 12LAE50CF003 | HP DESUPERHEATER SPRAY FT 2 |  | -621.6 | 621.6 | 0 | 524 | mBar | ROSEMOUNT | 2051 PT | 214466 |  |  | ZM06 |  |  | 12LAE50GH101
271 | KIPP12 | 12LAF40CF002 | RH DESUPERHEATER SPRAY FT 1 |  | -635 | 635 | 0 | 322 | mbar | ROSEMOUNT | 2051 PT | 214480 |  |  | ZM06 |  |  | 12LAB46GH101
272 | KIPP12 | 12LAF40CF003 | RH DESUPERHEATER SPRAY FT 2 |  | -635 | 635 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214481 |  |  | ZM06 |  |  | 12LAB46GH101
273 | KIPP12 | 12LBA00CP101 | HIGH PRESSURE STEAM PRESSURE | 2026-03-17 | -1 | 500 | 0 | 151 | Bar | ROSEMOUNT | EJA530E | 91S313316 |  |  | ZM06
274 | KIPP12 | 12LBA10CF002 | LP STEAM O/L FT 1 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214635 |  |  | ZM06 |  |  | 12LAB96GH101
275 | KIPP12 | 12LBA10CF003 | LP STEAM O/L FT 2 | 2026-03-16 | -621.6 | 621.6 | 0 | 115 | mBar | ROSEMOUNT | 2051 PT | 214636 |  |  | ZM06 |  |  | 12LAB96GH101
276 | KIPP12 | 12LBA10CP001 | LP STEAM PT | 2026-03-24 | -1 | 55.16 | 0 | 15 | Bar | ROSEMOUNT | 2051 PT | 210454 |  |  | ZM06 |  |  | 12LAB96GH101
277 | KIPP12 | 12LBA20CP101 | HP BYPASS VALVE OUTLET PRESSURE A | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313284 |  |  | ZM06
278 | KIPP12 | 12LBA20CP102 | HP BYPASS VALVE OUTLET PRESSURE B | 2026-03-17 | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S313285 |  |  | ZM06
279 | KIPP12 | 12LBA30CF002 | IP STEAM O/L FT 1 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214482 |  |  | ZM06 |  |  | 12LBA30GH101
280 | KIPP12 | 12LBA30CF003 | IP STEAM O/L FT 2 |  | -621.6 | 621.6 | 0 | 322 | mBar | ROSEMOUNT | 2051 PT | 214483 |  |  | ZM06 |  |  | 12LBA30GH101
281 | KIPP12 | 12LBA30CP001 | IP STEAM O/L PT |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210449 |  |  | ZM06 |  |  | 12LBA30GH101
282 | KIPP12 | 12LBA31CP101 | LP STEAM PT | 2026-03-24 | -1 | 20 | 0 | 10 | Bar | YOKOGAWA | EJA530E | 91S313229 |  |  | ZM06
283 | KIPP12 | 12LBA40CP101 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313230 |  |  | ZM06
284 | KIPP12 | 12LBA40CP102 | LP STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 4 | Bar | YOKOGAWA | EJA530E | 91S313231 |  |  | ZM06
285 | KIPP12 | 12LBA50CF002 | HP STEAM O/L FT 1 |  | -2468 | 2468 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214476 |  |  | ZM06 |  |  | 12LBC00GH101
286 | KIPP12 | 12LBA50CF003 | HP STEAM O/L FT 2 |  | -2468 | 2468 | 0 | 1600 | mBar | ROSEMOUNT | 2051 PT | 214477 |  |  | ZM06 |  |  | 12LBC00GH101
287 | KIPP12 | 12LBA50CP001 | HP STEAM PT |  | 0 | 689.5 | 0 | 200 | Bar | ROSEMOUNT | 2051 PT | 210443 |  |  | ZM06
288 | KIPP12 | 12LBB00CP101 | HOT REHEAT STEAM PT | 2026-03-17 | -1 | 500 | 0 | 50 | Bar | YOKOGAWA | EJA530E | 91S313215 |  |  | ZM06
289 | KIPP12 | 12LBB20CP101 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313224 |  |  | ZM06
290 | KIPP12 | 12LBB20CP102 | HOT REHEAT STEAM BYPASS VALVE OUTLET PT | 2026-03-23 | -1 | 20 | 0 | 13 | Bar | YOKOGAWA | EJA530E | 91S313225 |  |  | ZM06
291 | KIPP12 | 12LBB40CP001 | RH STEAM PT |  | -1.01 | 275.79 | 0 | 50 | Bar | ROSEMOUNT | 2051 PT | 210450 |  |  | ZM06 |  |  | 12LBA30GH101
292 | KIPP12 | 12LBC00CF101 | COLD REHEAT STEAM FLOW A |  | -10197.2 | 10197.2 | 0 | 2312 | mmH2O | YOKOGAWA | EJA110E | 91S313073 |  |  | ZM06 |  |  | 12LBC00GH101
293 | KIPP12 | 12LBC00CF102 | COLD REHEAT STEAM FLOW B |  | -10197.2 | 10197.2 | 0 | 2312 | mmH2O | YOKOGAWA | EJA110E | 91S313074 |  |  | ZM06 |  |  | 12LBC00GH101
294 | KIPP12 | 12LBC00CP101 | COLD REHEAT STEAM PRESSURE |  | -1 | 100 | 0 | 43 | Bar | YOKOGAWA | EJA530E | 91S213288 |  |  | ZM06 |  |  | 12LBC00GH101
295 | KIPP12 | 12LBC30CP001 | COLD REHEAT PRESSURE |  | -1.01 | 275.79 | 0 | 60 | Bar | ROSEMOUNT | 2051 PT | 210451 |  |  | ZM06 |  |  | 12HAC58GH101
296 | KIPP12 | 12LBG91CP001 | GT OTC OUT STEAM LINE PT-1 |  | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S213325 |  |  | ZM06
297 | KIPP12 | 12LBG91CP002 | GT OTC OUT STEAM LINE PT-1 |  | -1 | 500 | 0 | 192 | Bar | YOKOGAWA | EJA530E | 91S213327 |  |  | ZM06
298 | KIPP12 | 12LCA20CF101 | LP STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313063 |  |  | ZM06
299 | KIPP12 | 12LCA21CF101 | HOT REHEAT STEAM BYPASS SPRAYAY WATER FT | 2026-03-16 | -10197.2 | 10197.2 | 0 | 5000 | mmH2O | YOKOGAWA | EJA110E | 91S313061 |  |  | ZM06
300 | KIPP12 | 12MBA30CP001 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824808 |  |  | ZM06
301 | KIPP12 | 12MBA30CP003 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824809 |  |  | ZM06
302 | KIPP12 | 12MBA30CP004 | PRESSURE MEASUREMENT EXHAUST DIFFUSER |  | 0 | 2.0684 | 0.8 | 1.2 | Bar | ROSEMOUNT | 3051 PT | 9824810 |  |  | ZM06
303 | KIPP12 | 12MBA80CP051 | GT AFT COMPRESSOR 1H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825265 |  |  | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
304 | KIPP12 | 12MBA80CP052 | GT AFT COMPRESSOR 4H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051CG | 9825266 |  |  | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
305 | KIPP12 | 12MBA80CP054 | P AFT COMPRESSOR 8H PT |  | -137.89 | 137.89 | 0 | 40 | Bar | ROSEMOUNT | 3051 | 9825267 |  |  | ZM06 |  | 3051CG5A22A1BE8Q4CTA9258
306 | KIPP12 | 12MBE41CP013 | GT H/F WATER PUMP SUCTION FILTER PDT |  | 0 | 0 | -1000 | 2200 | mBar | ROSEMOUNT | 2088TG | 2753519 |  |  | ZM06
307 | KIPP12 | 1: 12MBE41CP121; 2: GT H/F WATER PUMP-1 SUCTION PT; 4: -14.7; 5: 800; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 210447
308 | KIPP12 | 1: 12MBE41CP122; 2: GT H/F WATER PUMP-2 SUCTION PT; 4: -14.7; 5: 4000; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 210453
309 | KIPP12 | 1: 12MBE41CP123; 2: GT H/F WATER PUMP-3 SUCTION PT; 4: -14.7; 5: 800; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 10195290
310 | KIPP12 | 1: 12MBE41CP124; 2: GT H/F WATER PUMP-4 SUCTION PT; 4: -14.7; 5: 4000; 6: -14.7; 7: 150; 8: psi; 9: ROSEMOUNT; 10: 2051TG; 11: 10195289
311 | KIPP12 | 1: 12MBE41CP141; 2: GT H/F WATER PUMP-1 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631491
312 | KIPP12 | 1: 12MBE41CP142; 2: GT H/F WATER PUMP-2 DISCHARGE PT; 4: -14.7; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631489
313 | KIPP12 | 1: 12MBE41CP143; 2: GT H/F WATER PUMP-3 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631490
314 | KIPP12 | 1: 12MBE41CP144; 2: GT H/F WATER PUMP-4 DISCHARGE PT; 4: 0; 5: 4000; 6: -14.7; 7: 4000; 8: psi; 9: ROSEMOUNT; 10: 2088TG; 11: 631487
315 | KIPP12 | 12MBH20CP007 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825271 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
316 | KIPP12 | 12MBH20CP008 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825272 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
317 | KIPP12 | 12MBH20CP009 | GT COOLING AIR CARR PT |  | -137.89 | 137.89 | 0 | 15 | Bar | ROSEMOUNT | 3051 | 9825273 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
318 | KIPP12 | 1: 12MBH30CL001; 2: LP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313553
319 | KIPP12 | 1: 12MBH30CL002; 2: LP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313554
320 | KIPP12 | 12MBH30CP003 | P SEV COMBUSTOR PLENUM/KA01 |  | -137.89 | 137.89 | 0 | 25 | Bar | YOKOGAWA | 3051 | 9825268 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
321 | KIPP12 | 12MBH30CP004 | P SEV COMBUSTOR PLENUM/KA01 |  | 137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825269 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
322 | KIPP12 | 12MBH30CP005 | P SEV COMBUSTOR PLENUM/KA01 |  | 137.89 | 137.89 | 0 | 25 | Bar | ROSEMOUNT | 3051 | 9825270 |  |  |  |  | 3051CG5A22A1BE8Q4CTA9258
323 | KIPP12 | 1: 12MBH30CP015; 2: PRESSURE DIFF ACROSS LP AIR COOLER; 4: -20.684; 5: 20.684; 6: 0; 7: 4; 8: Bar; 9: ROSEMOUNT; 10: 3051; 11: 9824812
324 | KIPP12 | 1: 12MBH30CP020; 2: P QUENSCH WATER TO LP COOLER; 4: 137.89; 5: 137.89; 6: 0; 7: 30; 8: Bar; 9: ROSEMOUNT; 10: 3051; 11: 9825289
325 | KIPP12 | 12MBH30CP021 | DP SEV COMBUSTOR LINER |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825279 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
326 | KIPP12 | 12MBH30CP022 | P DIFF SEV COMBUSTOR LINER/KA01 |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825277 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
327 | KIPP12 | 12MBH30CP023 | P DIFF SEV COMBUSTOR LINER/KA01 |  | -20.684 | 20.684 | 0 | 5 | Bar | ROSEMOUNT | 3051 | 9825278 |  |  |  |  | 3051CD4A22A1BE8Q4CTA9258
328 | KIPP12 | 1: 12MBH40CL001; 2: HP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313551
329 | KIPP12 | 1: 12MBH40CL002; 2: HP OTC DIFFRENTIAL LEVEL TRANSMITTER; 4: -5; 5: 5; 6: 0; 7: -2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313552
330 | KIPP12 | 1: 12MBH40CP015; 2: DP HP OTC; 4: -621.6; 5: 621.6; 6: 0; 7: 500; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9825291
331 | KIPP12 | 1: 12MBH41CP102; 2: PRESSURE AFTER BLOW-OFF BYPASS VALVE; 4: -137.89; 5: 137.89; 6: 0; 7: 40; 8: Bar; 9: ROSEMOUNT; 10: 3051CD
332 | KIPP12 | 1: 12MBH41CP103; 2: DP FLOW MEASUREMENT; 4: -20.684; 5: 20.684; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 3051CD
333 | KIPP12 | 1: 12MBH52CP001; 2: EXHAUST BEARING FAN 1 PDI; 4: -621.6; 5: 621.6; 6: 0; 7: 400; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891375
334 | KIPP12 | 1: 12MBH52CP002; 2: EXHAUST BEARING FAN 2 PDI; 4: -621.6; 5: 621.6; 6: 0; 7: 400; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891376
335 | KIPP12 | 1: 12MBH60CP001; 2: DP CMAS FAN 1; 4: -621.6; 5: 621.6; 6: 0; 7: 50; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891373
336 | KIPP12 | 1: 12MBH60CP002; 2: DP CMAS FAN 2; 4: -621.6; 5: 621.6; 6: 0; 7: 50; 8: mBar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9891374
337 | KIPP12 | 1: 12MBH80CP011; 2: DIFFERENTIAL PRESSURE EV COMBUSTOR; 4: -2.4864; 5: 2.4864; 6: 0; 7: 2.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9825282
338 | KIPP12 | 1: 12MBH80CP012; 2: DIFFERENTIAL PRESSURE EV COMBUSTOR; 4: -2.4864; 5: 2.4864; 6: 0; 7: 2.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9825283
339 | KIPP12 | 1: 12MBH90CP001; 2: PRESSURE BEFORE ANTI-ICING CONTROL VALVE; 4: -137.89; 5: 137.89; 6: 0; 7: 40; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9914215
340 | KIPP12 | 1: 12MBH90CP004; 2: DP OVER ANTI ICING CV; 4: -137.89; 5: 137.89; 6: 0; 7: 40; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9914217
341 | KIPP12 | 1: 12MBL01CP011; 2: DP AIR INTK FLTR TOT; 4: -621.6; 5: 621.6; 6: 0; 7: 3000; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 98426871
342 | KIPP12 | 1: 12MBL01CP012; 2: DP AIR INTK FLTR TOT; 4: -621.6; 5: 621.6; 6: 0; 7: 3000; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844814
343 | KIPP12 | 1: 12MBL51CP001; 2: DP PRE FLTR STAGE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844808
344 | KIPP12 | 1: 12MBL51CP002; 2: DP FINE FLTR STAGE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844809
345 | KIPP12 | 1: 12MBL51CP012; 2: DP FINE FLTR STAGE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9844810
346 | KIPP12 | 1: 12MBL61CP010; 2: EVAP COOLER PUMP AFTER PRESSURE; 4: -621.6; 5: 621.6; 6: 0; 7: 2500; 8: Pa; 9: ROSEMOUNT; 10: 3051 PT; 11: 9852955
347 | KIPP12 | 1: 12MBP01CP003; 2: FUEL GAS FILTER DP; 4: -2.4864; 5: 2.4864; 6: 0; 7: 1.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9789263
348 | KIPP12 | 12MBP05CP102 | EV FUEL GAS FLOW PT |  | 0 | 55.16 | 0 | 55 | Bar | ROSEMOUNT | 3051 PT | 9846442 | [6 empty] | Atm. Basıncı 0,935 Bar
349 | KIPP12 | 1: 12MBP41CP001; 2: P AFT TRIP SOV EV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782037
350 | KIPP12 | 1: 12MBP41CP004; 2: DP CV EV STG2; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782043
351 | KIPP12 | 1: 12MBP41CP006; 2: P AFT CV FGAS EV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782038
352 | KIPP12 | 1: 12MBP42CP001; 2: P BEF FGAS TRIP SOV SEV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782039
353 | KIPP12 | 1: 12MBP42CP004; 2: DP CV FGAS SEV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782044
354 | KIPP12 | 1: 12MBP42CP006; 2: P AFT CV FGAS SEV; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782040
355 | KIPP12 | 1: 12MBP43CP001; 2: P BFR CV EV STG1 FGAS; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782041
356 | KIPP12 | 1: 12MBP43CP004; 2: DP CV EVSTG1 FGAS; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782045
357 | KIPP12 | 1: 12MBP43CP006; 2: P AFT CV EV STG1 FGAS; 4: -137.89; 5: 137.89; 6: 0; 7: 70; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782042
358 | KIPP12 | 1: 12MBV10CP001; 2: PRESSURE LUBE OIL TANK; 4: -62.16; 5: 62.16; 6: 0; 7: 60; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782022
359 | KIPP12 | 1: 12MBV21CP001; 2: P AFT LUBE OIL PMP 1; 4: -1.013; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791825
360 | KIPP12 | 1: 12MBV21CP002; 2: P AFT LUBE OIL PMP 2; 4: -1.013; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791826
361 | KIPP12 | 1: 12MBV21CP003; 2: LUBE OIL FILTER DP; 4: -2.4864; 5: 2.4864; 6: -2.5; 7: 2.5; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782023
362 | KIPP12 | 1: 12MBV22CP001; 2: EMERGENCY LUBE OIL PUMP AFTER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791827
363 | KIPP12 | 1: 12MBV40CP001; 2: LUBE OIL HEADER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791828
364 | KIPP12 | 1: 12MBV40CP002; 2: LUBE OIL HEADER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791829
365 | KIPP12 | 1: 12MBV40CP003; 2: LUBE OIL HEADER PRESSURE; 4: -10.342; 5: 10.342; 6: 0; 7: 10; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791830
366 | KIPP12 | 1: 12MBV40CP006; 2: P LUBE OIL HEADER 6 ( PRESSURE SWITCH ); 4: 0; 5: 10; 6: 1.99; 7: 2.2; 8: Bar; 9: Trafog; 10: Switch; 11: -
367 | KIPP12 | 1: 12MBX21CP001; 2: P AFT PWR OIL PMP 1; 4: -1.01; 5: 55.16; 6: 0; 7: 52; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791831
368 | KIPP12 | 1: 12MBX21CP002; 2: P AFT PWR OIL PMP 2; 4: -1.01; 5: 55.16; 6: 0; 7: 52; 8: Bar; 9: ROSEMOUNT; 10: 2088 PT; 11: 9791832
369 | KIPP12 | 1: 12MBX21CP010; 2: GT P/O TWIN FILTER PDT; 4: -20.684; 5: 20.684; 6: -2; 7: 8; 8: Bar; 9: ROSEMOUNT; 10: 3051CD; 11: 9782046
370 | KIPP12 | 1: 12MBX42CP001; 2: P HYDR SAFETY SYS; 4: -137.89; 5: 137.89; 6: 0; 7: 60; 8: Bar; 9: ROSEMOUNT; 10: 3051 PT; 11: 9782047
371 | KIPP12 | 1: 12LAB90CP001; 2: FEED WATER TO GT OTC STRAINER PDT; 4: -5; 5: 5; 6: 0; 7: 2; 8: Bar; 9: YOKOGAWA; 10: EJA110E; 11: 91S313546
372 | KIPP12 | 12LAB91CF101 | FW LP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816774
373 | KIPP12 | 12LAB91CF102 | FW LP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 600 | mBar | ROSEMOUNT | 3051CD | 9816937
374 | KIPP12 | 12LAB92CF101 | FW HP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816776
375 | KIPP12 | 12LAB92CF102 | FW HP OTC FITCA | 2026-03-16 | -2486.4 | 2486.4 | 0 | 250 | mBar | ROSEMOUNT | 3051CD | 9816777
376
377
378
379
380

## Tx List (2) (hidden)
No | Functional Location | Description | Calibration Date | Sensor LRV | Sensor URV | Calibrated LRV | Calibrated URV | Unit | Customer | Sensor Model | Tx Serial No. | Tx Status | SAP Ekipman Kodu | Order Type | SAP Status | Panel KKS | Comments
1 | KIPP12MBV21CP001 |  |  | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791825 | Waiting |  |  |  |  | Out of SAP list | KIPP00GHC10CP101
2 | KIPP12MBV21CP002 |  |  | -1.013 | 10.342 | 0 | 10 | Bar | ROSEMOUNT | 2088 PT | 9791826 | Waiting |  |  |  |  | Out of SAP list | KIPP00GHC10CP102
3 | KIPP12MBL61CP010 |  |  | -6216 | 6216 | 0 | 1000 | Pa | ROSEMOUNT | 3051 PT | 9852955 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAA00CP101
4 | KIPP10LCA10CF102 | CONDENSATE EXTRACTION PUMP DISCHARGE FT |  | -10197.2 | 10197.2 | 0 | 10000 | mmH2O | YOKOGAWA | EJA110E | 91S313101 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAA00CP102
5 | KIPP10LCA01CP101 | CEP-A SUC. Filter PRESS. | 2020-02-16 | -5000 | 5000 | 0 | 500 | mBar | YOKOGAWA | EJA110E | 91S313075 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAA00CP103
6 | KIPP10LCA02CP101 | CEP-B SUC. Filter PRESS. | 2020-02-16 | -5000 | 5000 | 0 | 500 | mBar | YOKOGAWA | EJA110E | 91S313076 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAB01CP102
7 | KIPP10LCA03CP101 | CEP-C SUC. Filter PRESS. | 2020-02-16 | -5000 | 5000 | 0 | 500 | mBar | YOKOGAWA | EJA110E | 91S313077 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAB02CP102
8 | 11HAC58CP001 | HP DRUM FW PT |  | 0 | 689.5 | 0 | 300 | Bar | ROSEMOUNT | 2051 PT | 210420 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAB03CP102
9 | 11HAC58CF002 | HP DRUM FW FLOW A |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 PT | 214452 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAB06CP102
10 | 11HAC58CF003 | HP DRUM FW FLOW B |  | -621.6 | 621.6 | 0 | 302 | mBar | ROSEMOUNT | 2051 PT | 214453 | Waiting |  |  |  |  | Out of SAP list | KIPP10LAB07CP102
11 | [11 empty] | Waiting | [5 empty] | KIPP10LAB08CP102
12 | [11 empty] | Waiting | [5 empty] | KIPP10LAB10CP101
13 | [11 empty] | Waiting | [5 empty] | KIPP10LAB10CP102
14 | [11 empty] | Waiting | [5 empty] | KIPP10LAB11CP101
15 | [11 empty] | Waiting | [5 empty] | KIPP10LAB12CP101
16 | [11 empty] | Waiting | [5 empty] | KIPP10LAB13CP101
17 | [11 empty] | Waiting | [5 empty] | KIPP10LAB15CP101
18 | [11 empty] | Waiting | [5 empty] | KIPP10LAB15CP102
19 | [11 empty] | Waiting | [5 empty] | KIPP10LAB16CP101
20 | [11 empty] | Waiting | [5 empty] | KIPP10LAB17CP101
21 | [11 empty] | Waiting | [5 empty] | KIPP10LAB18CP101
22 | [11 empty] | Waiting | [5 empty] | KIPP10LAB30CP101
23 | [11 empty] | Waiting | [5 empty] | KIPP10LAB30CP102
24 | [11 empty] | Waiting | [5 empty] | KIPP10LAB31CP101
25 | [11 empty] | Waiting | [5 empty] | KIPP10LAB32CP101
26 | [11 empty] | Waiting | [5 empty] | KIPP10LAB33CP101
27 | [11 empty] | Waiting | [5 empty] | KIPP10LBA10CP001
28 | [11 empty] | Waiting | [5 empty] | KIPP10LBA10CP002
29 | [11 empty] | Waiting | [5 empty] | KIPP10LBA50CP001
30 | [11 empty] | Waiting | [5 empty] | KIPP10LBA50CP002
31 | [11 empty] | Waiting | [5 empty] | KIPP10LBB41CP001
32 | [11 empty] | Waiting | [5 empty] | KIPP10LBB42CP001
33 | [11 empty] | Waiting | [5 empty] | KIPP10LBC10CP001
34 | [11 empty] | Waiting | [5 empty] | KIPP10LBC10CP002
35 | [11 empty] | Waiting | [5 empty] | KIPP10LBC10CP003
36 | [11 empty] | Waiting | [5 empty] | KIPP10LBC10CP101
37 | [11 empty] | Waiting | [5 empty] | KIPP10LBG00CP101
38 | [11 empty] | Waiting | [5 empty] | KIPP10LBG00CP102
39 | [11 empty] | Waiting | [5 empty] | KIPP10LCA01CP102
40 | [11 empty] | Waiting | [5 empty] | KIPP10LCA02CP102
41 | [11 empty] | Waiting | [5 empty] | KIPP10LCA03CP102
42 | [11 empty] | Waiting | [5 empty] | KIPP10LCA10CP101
43 | [11 empty] | Waiting | [5 empty] | KIPP10LCA10CP102
44 | [11 empty] | Waiting | [5 empty] | KIPP10LCA10CP103
45 | [11 empty] | Waiting | [5 empty] | KIPP10LCA11CP101
46 | [11 empty] | Waiting | [5 empty] | KIPP10LCA12CP101
47 | [11 empty] | Waiting | [5 empty] | KIPP10LCA13CP101
48 | [11 empty] | Waiting | [5 empty] | KIPP11HAD10CP001
49 | [11 empty] | Waiting | [5 empty] | KIPP11HAD10CP002
50 | [11 empty] | Waiting | [5 empty] | KIPP11HAD10CP003
51 | [11 empty] | Waiting | [5 empty] | KIPP11HAD30CP001
52 | [11 empty] | Waiting | [5 empty] | KIPP11HAD30CP002
53 | [11 empty] | Waiting | [5 empty] | KIPP11HAD30CP003
54 | [11 empty] | Waiting | [5 empty] | KIPP11HAD50CP001
55 | [11 empty] | Waiting | [5 empty] | KIPP11HAD50CP002
56 | [11 empty] | Waiting | [5 empty] | KIPP11HAD50CP003
57 | [11 empty] | Waiting | [5 empty] | KIPP11LAB46CP001
58 | [11 empty] | Waiting | [5 empty] | KIPP11LAB96CP001
59 | [11 empty] | Waiting | [5 empty] | KIPP11LBA00CP101
60 | [11 empty] | Waiting | [5 empty] | KIPP11LBA10CP001
61 | [11 empty] | Waiting | [5 empty] | KIPP11LBA20CP101
62 | [11 empty] | Waiting | [5 empty] | KIPP11LBA20CP102
63 | [11 empty] | Waiting | [5 empty] | KIPP11LBA30CP001
64 | [11 empty] | Waiting | [5 empty] | KIPP11LBA31CP101
65 | [11 empty] | Waiting | [5 empty] | KIPP11LBA40CP101
66 | [11 empty] | Waiting | [5 empty] | KIPP11LBA40CP102
67 | [11 empty] | Waiting | [5 empty] | KIPP11LBA50CP001
68 | [11 empty] | Waiting | [5 empty] | KIPP11LBB00CP101
69 | [11 empty] | Waiting | [5 empty] | KIPP11LBB20CP101
70 | [11 empty] | Waiting | [5 empty] | KIPP11LBB20CP102
71 | [11 empty] | Waiting | [5 empty] | KIPP11LBB40CP001
72 | [11 empty] | Waiting | [5 empty] | KIPP11LBC00CP101
73 | [11 empty] | Waiting | [5 empty] | KIPP11LBC30CP001
74 | [11 empty] | Waiting | [5 empty] | KIPP11LBG91CP001
75 | [11 empty] | Waiting | [5 empty] | KIPP11LBG91CP002
76 | [11 empty] | Waiting | [5 empty] | KIPP12HAD10CP001
77 | [11 empty] | Waiting | [5 empty] | KIPP12HAD10CP002
78 | [11 empty] | Waiting | [5 empty] | KIPP12HAD10CP003
79 | [11 empty] | Waiting | [5 empty] | KIPP12HAD30CP001
80 | [11 empty] | Waiting | [5 empty] | KIPP12HAD30CP002
81 | [11 empty] | Waiting | [5 empty] | KIPP12HAD30CP003
82 | [11 empty] | Waiting | [5 empty] | KIPP12HAD50CP001
83 | [11 empty] | Waiting | [5 empty] | KIPP12HAD50CP002
84 | [11 empty] | Waiting | [5 empty] | KIPP12HAD50CP003
85 | [11 empty] | Waiting | [5 empty] | KIPP12LAB46CP001
86 | [11 empty] | Waiting | [5 empty] | KIPP12LAB96CP001
87 | [11 empty] | Waiting | [5 empty] | KIPP12LBA00CP101
88 | [11 empty] | Waiting | [5 empty] | KIPP12LBA10CP001
89 | [11 empty] | Waiting | [5 empty] | KIPP12LBA20CP101
90 | [11 empty] | Waiting | [5 empty] | KIPP12LBA20CP102
91 | [11 empty] | Waiting | [5 empty] | KIPP12LBA30CP001
92 | [11 empty] | Waiting | [5 empty] | KIPP12LBA31CP101
93 | [11 empty] | Waiting | [5 empty] | KIPP12LBA40CP101
94 | [11 empty] | Waiting | [5 empty] | KIPP12LBA40CP102
95 | [11 empty] | Waiting | [5 empty] | KIPP12LBA50CP001
96 | [11 empty] | Waiting | [5 empty] | KIPP12LBB00CP101
97 | [11 empty] | Waiting | [5 empty] | KIPP12LBB20CP101
98 | [11 empty] | Waiting | [5 empty] | KIPP12LBB20CP102
99 | [11 empty] | Waiting | [5 empty] | KIPP12LBB40CP001
100 | [11 empty] | Waiting | [5 empty] | KIPP12LBC00CP101
101 | [11 empty] | Waiting | [5 empty] | KIPP12LBC30CP001
102 | [11 empty] | Waiting | [5 empty] | KIPP12LBG91CP001
103 | [11 empty] | Waiting | [5 empty] | KIPP12LBG91CP002
104 | [11 empty] | Waiting | [5 empty] | KIPP00GHC24CF101
105 | [11 empty] | Waiting | [5 empty] | KIPP10LAB11CF101
106 | [11 empty] | Waiting | [5 empty] | KIPP10LAB11CF102
107 | [11 empty] | Waiting | [5 empty] | KIPP10LAB12CF101
108 | [11 empty] | Waiting | [5 empty] | KIPP10LAB12CF102
109 | [11 empty] | Waiting | [5 empty] | KIPP10LAB13CF101
110 | [11 empty] | Waiting | [5 empty] | KIPP10LAB13CF102
111 | [11 empty] | Waiting | [5 empty] | KIPP10LAB24CF101
112 | [11 empty] | Waiting | [5 empty] | KIPP10LCA10CF101
113 | [11 empty] | Waiting | [5 empty] | KIPP10LCA10CF102
114 | [11 empty] | Waiting | [5 empty] | KIPP10LCA20CF101
115 | [11 empty] | Waiting | [5 empty] | KIPP11HAC22CF002
116 | [11 empty] | Waiting | [5 empty] | KIPP11HAC22CF003
117 | [11 empty] | Waiting | [5 empty] | KIPP11LAB20CF101
118 | [11 empty] | Waiting | [5 empty] | KIPP11LAB31CF101
119 | [11 empty] | Waiting | [5 empty] | KIPP10MAA10CT031A
120 | [11 empty] | Waiting | [5 empty] | KIPP10MAA10CT031B
121 | [11 empty] | Waiting | [5 empty] | KIPP10MAW10CT001
122 | [11 empty] | Waiting | [5 empty] | KIPP10MAW10CT002
123 | [11 empty] | Waiting | [5 empty] | KIPP10MAA10CP001
124 | [11 empty] | Waiting | [5 empty] | KIPP10MAB10CP001
125 | [11 empty] | Waiting | [5 empty] | KIPP10MAB10CP002
126 | [11 empty] | Waiting | [5 empty] | KIPP10MAC01CP021
127 | [11 empty] | Waiting | [5 empty] | KIPP10MAC01CP022
128 | [11 empty] | Waiting | [5 empty] | KIPP10MAC10CP031
129 | [11 empty] | Waiting | [5 empty] | KIPP10MAC10CP032
130 | [11 empty] | Waiting | [5 empty] | KIPP10MAC10CP033
131 | [11 empty] | Waiting | [5 empty] | KIPP10MAV40CP003
132 | [11 empty] | Waiting | [5 empty] | KIPP10MAV40CP004
133 | [11 empty] | Waiting | [5 empty] | KIPP10MAV40CP005
134 | [11 empty] | Waiting | [5 empty] | KIPP10MAW02CP001
135 | [11 empty] | Waiting | [5 empty] | KIPP10MAW15CP001
136 | [11 empty] | Waiting | [5 empty] | KIPP10MAX11CP031
137 | [11 empty] | Waiting | [5 empty] | KIPP10MAX44CP001
138 | [11 empty] | Waiting | [5 empty] | KIPP10MAX44CP002
139 | [11 empty] | Waiting | [5 empty] | KIPP10MAX44CP003
140 | [11 empty] | Waiting | [5 empty] | KIPP11MBA80CP007
141 | [11 empty] | Waiting | [5 empty] | KIPP11MBA80CP008
142 | [11 empty] | Waiting | [5 empty] | KIPP11MBV40CP006
143 | [11 empty] | Waiting | [5 empty] | KIPP10MKA13CP111
144 | [11 empty] | Waiting | [5 empty] | KIPP10MKA13CP112
145 | [11 empty] | Waiting | [5 empty] | KIPP10MKA13CP113
146 | [11 empty] | Waiting | [5 empty] | KIPP11EKG40CP101
147 | [11 empty] | Waiting | [5 empty] | KIPP11MBA30CP001
148 | [11 empty] | Waiting | [5 empty] | KIPP11MBA30CP003
149 | [11 empty] | Waiting | [5 empty] | KIPP11MBA30CP004
150 | [11 empty] | Waiting | [5 empty] | KIPP11MBH30CL001
151 | [11 empty] | Waiting | [5 empty] | KIPP11MBH30CL002
152 | [11 empty] | Waiting | [5 empty] | KIPP11MBH30CP003
153 | [11 empty] | Waiting | [5 empty] | KIPP11MBH30CP004
154 | [11 empty] | Waiting | [5 empty] | KIPP11MBH30CP005
155 | [11 empty] | Waiting | [5 empty] | KIPP11MBH30CP015
156 | [11 empty] | Waiting | [5 empty] | KIPP11MBH30CP020
157 | [11 empty] | Waiting | [5 empty] | KIPP11MBH40CL001
158 | [11 empty] | Waiting | [5 empty] | KIPP11MBH40CL002
159 | [11 empty] | Waiting | [5 empty] | KIPP11MBH40CP015
160 | [11 empty] | Waiting | [5 empty] | KIPP11MBH52CP001
161 | [11 empty] | Waiting | [5 empty] | KIPP11MBH60CP001
162 | [11 empty] | Waiting | [5 empty] | KIPP11MBH80CP011
163 | [11 empty] | Waiting | [5 empty] | KIPP11MBH80CP012
164 | [11 empty] | Waiting | [5 empty] | KIPP11MBH90CP001
165 | [11 empty] | Waiting | [5 empty] | KIPP11MBH90CP004
166 | [11 empty] | Waiting | [5 empty] | KIPP11MBL01CP011
167 | [11 empty] | Waiting | [5 empty] | KIPP11MBL01CP012
168 | [11 empty] | Waiting | [5 empty] | KIPP11MBL51CP001
169 | [11 empty] | Waiting | [5 empty] | KIPP11MBL51CP002
170 | [11 empty] | Waiting | [5 empty] | KIPP11MBL51CP012
171 | [11 empty] | Waiting | [5 empty] | KIPP11MBP01CP003
172 | [11 empty] | Waiting | [5 empty] | KIPP11MBP05CP102
173 | [11 empty] | Waiting | [5 empty] | KIPP11MBP41CP001
174 | [11 empty] | Waiting | [5 empty] | KIPP11MBP41CP004
175 | [11 empty] | Waiting | [5 empty] | KIPP11MBP41CP006
176 | [11 empty] | Waiting | [5 empty] | KIPP11MBP42CP001
177 | [11 empty] | Waiting | [5 empty] | KIPP11MBP42CP004
178 | [11 empty] | Waiting | [5 empty] | KIPP11MBP42CP006
179 | [11 empty] | Waiting | [5 empty] | KIPP11MBP43CP001
180 | [11 empty] | Waiting | [5 empty] | KIPP11MBP43CP004
181 | [11 empty] | Waiting | [5 empty] | KIPP11MBP43CP006
182 | [11 empty] | Waiting | [5 empty] | KIPP11MBV10CP001
183 | [11 empty] | Waiting | [5 empty] | KIPP11MBV21CP003
184 | [11 empty] | Waiting | [5 empty] | KIPP11MBV22CP001
185 | [11 empty] | Waiting | [5 empty] | KIPP11MBV40CP001
186 | [11 empty] | Waiting | [5 empty] | KIPP11MBV40CP002
187 | [11 empty] | Waiting | [5 empty] | KIPP11MBV40CP003
188 | [11 empty] | Waiting | [5 empty] | KIPP11MBX21CP001
189 | [11 empty] | Waiting | [5 empty] | KIPP11MBX21CP002
190 | [11 empty] | Waiting | [5 empty] | KIPP11MBX42CP001
191 | [11 empty] | Waiting | [5 empty] | KIPP12MBA80CP007
192 | [11 empty] | Waiting | [5 empty] | KIPP12MBA80CP008
193 | [11 empty] | Waiting | [5 empty] | KIPP12MBV40CP006
194 | [11 empty] | Waiting | [5 empty] | KIPP12EKG40CP101
195 | [11 empty] | Waiting | [5 empty] | KIPP12MBA30CP001
196 | [11 empty] | Waiting | [5 empty] | KIPP12MBA30CP003
197 | [11 empty] | Waiting | [5 empty] | KIPP12MBA30CP004
198 | [11 empty] | Waiting | [5 empty] | KIPP12MBH30CL001
199 | [11 empty] | Waiting | [5 empty] | KIPP12MBH30CL002
200 | [11 empty] | Waiting | [5 empty] | KIPP12MBH30CP003
201 | [11 empty] | Waiting | [5 empty] | KIPP12MBH30CP004
202 | [11 empty] | Waiting | [5 empty] | KIPP12MBH30CP005
203 | [11 empty] | Waiting | [5 empty] | KIPP12MBH30CP015
204 | [11 empty] | Waiting | [5 empty] | KIPP12MBH30CP020
205 | [11 empty] | Waiting | [5 empty] | KIPP12MBH40CL001
206 | [11 empty] | Waiting | [5 empty] | KIPP12MBH40CL002
207 | [11 empty] | Waiting | [5 empty] | KIPP12MBH40CP015
208 | [11 empty] | Waiting | [5 empty] | KIPP12MBH52CP001
209 | [11 empty] | Waiting | [5 empty] | KIPP12MBH60CP001
210 | [11 empty] | Waiting | [5 empty] | KIPP12MBH80CP011
211 | [11 empty] | Waiting | [5 empty] | KIPP12MBH80CP012
212 | [11 empty] | Waiting | [5 empty] | KIPP12MBH90CP001
213 | [11 empty] | Waiting | [5 empty] | KIPP12MBH90CP004
214 | [11 empty] | Waiting | [5 empty] | KIPP12MBL01CP011
215 | [11 empty] | Waiting | [5 empty] | KIPP12MBL01CP012
216 | [11 empty] | Waiting | [5 empty] | KIPP12MBL51CP001
217 | [11 empty] | Waiting | [5 empty] | KIPP12MBL51CP002
218 | [11 empty] | Waiting | [5 empty] | KIPP12MBL51CP012
219 | [11 empty] | Waiting | [5 empty] | KIPP12MBP01CP003
220 | [11 empty] | Waiting | [5 empty] | KIPP12MBP05CP102
221 | [11 empty] | Waiting | [5 empty] | KIPP12MBP41CP001
222 | [11 empty] | Waiting | [5 empty] | KIPP12MBP41CP004
223 | [11 empty] | Waiting | [5 empty] | KIPP12MBP41CP006
224 | [11 empty] | Waiting | [5 empty] | KIPP12MBP42CP001
225 | [11 empty] | Waiting | [5 empty] | KIPP12MBP42CP004
226 | [11 empty] | Waiting | [5 empty] | KIPP12MBP42CP006
227 | [11 empty] | Waiting | [5 empty] | KIPP12MBP43CP001
228 | [11 empty] | Waiting | [5 empty] | KIPP12MBP43CP004
229 | [11 empty] | Waiting | [5 empty] | KIPP12MBP43CP006
230 | [11 empty] | Waiting | [5 empty] | KIPP12MBV10CP001
231 | [11 empty] | Waiting | [5 empty] | KIPP12MBV21CP003
232 | [11 empty] | Waiting | [5 empty] | KIPP12MBV22CP001
233 | [11 empty] | Waiting | [5 empty] | KIPP12MBV40CP001
234 | [11 empty] | Waiting | [5 empty] | KIPP12MBV40CP002
235 | [11 empty] | Waiting | [5 empty] | KIPP12MBV40CP003
236 | [11 empty] | Waiting | [5 empty] | KIPP12MBX21CP001
237 | [11 empty] | Waiting | [5 empty] | KIPP12MBX21CP002
238 | [11 empty] | Waiting | [5 empty] | KIPP12MBX42CP001
239 | [11 empty] | Waiting | [5 empty] | KIPP12HAC22CF002
240 | [11 empty] | Waiting | [5 empty] | KIPP12HAC22CF003
241 | [11 empty] | Waiting | [5 empty] | KIPP12LAB20CF101
242 | [11 empty] | Waiting | [5 empty] | KIPP12LAB31CF101
243 | [11 empty] | Waiting | [5 empty] | KIPP12LAE50CF002
244 | [11 empty] | Waiting | [5 empty] | KIPP12LAE50CF003
245 | [11 empty] | Waiting | [5 empty] | KIPP12LAF40CF002
246 | [11 empty] | Waiting | [5 empty] | KIPP12LAF40CF003
247 | [11 empty] | Waiting | [5 empty] | KIPP12LBA10CF002
248 | [11 empty] | Waiting | [5 empty] | KIPP12LBA10CF003
249 | [11 empty] | Waiting | [5 empty] | KIPP12LBA30CF002
250 | [11 empty] | Waiting | [5 empty] | KIPP11LAE50CF002
251 | [11 empty] | Waiting | [5 empty] | KIPP11LAE50CF003
252 | [11 empty] | Waiting | [5 empty] | KIPP12LBA30CF003
253 | [11 empty] | Waiting | [5 empty] | KIPP12LBA50CF002
254 | [11 empty] | Waiting | [5 empty] | KIPP11LAF40CF002
255 | [11 empty] | Waiting | [5 empty] | KIPP11LAF40CF003
256 | [11 empty] | Waiting | [5 empty] | KIPP11LBA10CF002
257 | [11 empty] | Waiting | [5 empty] | KIPP11LBA10CF003
258 | [11 empty] | Waiting | [5 empty] | KIPP11LBA30CF002
259 | [11 empty] | Waiting | [5 empty] | KIPP11LBA30CF003
260 | [11 empty] | Waiting | [5 empty] | KIPP11LBA50CF002
261 | [11 empty] | Waiting | [5 empty] | KIPP12LBA50CF003
262 | [11 empty] | Waiting | [5 empty] | KIPP12LBC00CF101
263 | [11 empty] | Waiting | [5 empty] | KIPP12LBC00CF102
264 | [11 empty] | Waiting | [5 empty] | KIPP11LBA50CF003
265 | [11 empty] | Waiting | [5 empty] | KIPP12LCA20CF101
266 | [11 empty] | Waiting | [5 empty] | KIPP12LCA21CF101
267 | [11 empty] | Waiting | [5 empty] | KIPP11LBC00CF101
268 | [11 empty] | Waiting | [5 empty] | KIPP11LBC00CF102
269 | [11 empty] | Waiting | [5 empty] | KIPP11LCA20CF101
270 | [11 empty] | Waiting | [5 empty] | KIPP11LCA21CF101
271 | [11 empty] | Waiting | [5 empty] | KIPP10LAA00CL101
272 | [11 empty] | Waiting | [5 empty] | KIPP10LAA00CL102
273 | [11 empty] | Waiting | [5 empty] | KIPP10LAA00CL103
274 | [11 empty] | Waiting | [5 empty] | KIPP10LAA00CL104
275 | [11 empty] | Waiting | [5 empty] | KIPP10LAA00CL105
276 | [11 empty] | Waiting | [5 empty] | KIPP11HAD50CL001
277 | [11 empty] | Waiting | [5 empty] | KIPP11HAD50CL002
278 | [11 empty] | Waiting | [5 empty] | KIPP11HAD50CL003
279 | [11 empty] | Waiting | [5 empty] | KIPP11HAD30CL001
280 | [11 empty] | Waiting | [5 empty] | KIPP11HAD30CL002
281 | [11 empty] | Waiting | [5 empty] | KIPP11HAD30CL003
282 | [11 empty] | Waiting | [5 empty] | KIPP11HAD10CL001
283 | [11 empty] | Waiting | [5 empty] | KIPP11HAD10CL002
284 | [11 empty] | Waiting | [5 empty] | KIPP11HAD10CL003
285 | [11 empty] | Waiting | [5 empty] | KIPP12HAD50CL001
286 | [11 empty] | Waiting | [5 empty] | KIPP12HAD50CL002
287 | [11 empty] | Waiting | [5 empty] | KIPP12HAD50CL003
288 | [11 empty] | Waiting | [5 empty] | KIPP12HAD30CL001
289 | [11 empty] | Waiting | [5 empty] | KIPP12HAD30CL002
290 | [11 empty] | Waiting | [5 empty] | KIPP12HAD30CL003
291 | [11 empty] | Waiting | [5 empty] | KIPP12HAD10CL001
292 | [11 empty] | Waiting | [5 empty] | KIPP12HAD10CL002
293 | [11 empty] | Waiting | [5 empty] | KIPP12HAD10CL003
294 | [11 empty] | Waiting | [5 empty] | KIPP12HAC25CF002
295 | [11 empty] | Waiting | [5 empty] | KIPP12HAC25CF003
296 | [11 empty] | Waiting | [5 empty] | KIPP12MBV21CP001
297 | [11 empty] | Waiting | [5 empty] | KIPP12MBV21CP002
298 | [11 empty] | Waiting | [5 empty] | KIPP12MBL61CP010
299 | [11 empty] | Waiting | [5 empty] | KIPP10LCA01CP102
300 | [11 empty] | Waiting | [5 empty] | KIPP10LCA02CP102
301 | [11 empty] | Waiting | [5 empty] | KIPP10LCA03CP102
302 | [11 empty] | Waiting
303 | [11 empty] | Waiting
304 | [11 empty] | Waiting
305 | [11 empty] | Waiting
306 | [11 empty] | Waiting
307 | [11 empty] | Waiting
308 | [11 empty] | Waiting
309 | [11 empty] | Waiting
310 | [11 empty] | Waiting
311 | [11 empty] | Waiting
312 | [11 empty] | Waiting
313 | [11 empty] | Waiting
314 | [11 empty] | Waiting
315 | [11 empty] | Waiting
316 | [11 empty] | Waiting
317 | [11 empty] | Waiting
318 | [11 empty] | Waiting
319 | [11 empty] | Waiting
320 | [11 empty] | Waiting
321 | [11 empty] | Waiting
322 | [11 empty] | Waiting
323 | [11 empty] | Waiting
324 | [11 empty] | Waiting
325 | [11 empty] | Waiting
326 | [11 empty] | Waiting
327 | [11 empty] | Waiting
328 | [11 empty] | Waiting
329 | [11 empty] | Waiting
330 | [11 empty] | Waiting